## PS_IO_LIST_SCS_v4
Код | Title | Title_for_SIS | Loop | Typno | Loop No | IO Loop No | InterlockNO | Tag No | Service | Service_eng | Instrument Type | SCS | SCS_Old | Layout No | Location | I/O Type | Extype | Sub System | Auxiliary Instrument | Voltage Level | Power | Min | Max | Unit | Min1 | Max1 | Unit1 | LL | L | H | HH | HH2 | Unit3 | Rev | Remarks | Packgae | Rev Date | Rev Content | InterlockNO_Doc | MCC substations | Cable DCS | Cable Pair | Cable Type | Cable Length | Cable Description | JBOX | Cable Doc | Status | Cable NO | Control_cabinet | Mashalling_cabinet | Тег_CPU | Main_Chassis | Redundand_Chassis | Slot | Redundant_slot | Main_module | Main_module2 | Redundant_module | Redundant_module2 | Channel | SCS_распределение | D32_Вых | D32_Подмена | D32_Инверсия | D32_Вх_Аппертура | D32_Вх | Logical Group NO (Сегрегация) | Блокировка | TAG NO_CAE_CAUSE | DESCRIPTION_TAG_NO_CAE_CAUSE | Tag_Segr | Seg_St | Update1
2 | 3101 | 3101 | 3101-XZV-60507 | SDO0001-01 | 3101-XZV-60507 |  |  | 3101-XZY-60507 | Закрыть клапан пробки A в шредере для резины | Close the valve of plug A in rubber shredder | PLC signal | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6001B | PLC | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 2 | NEW | Rubber breaking system | ИД 2026 07 03 |  |  |  | 3101-S-JB-D112/3000-S-MC-B13 | PR04 | NH-KYJYP3 16x2.5 | 405 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D112 |  |  | 3101-XZY-60507/3101-S-JB-D112 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 10 | [12 empty] | Запись в БД произведена
3 | 3101 |  | 3101-MXI-60530 | SDO0001-01 | 3101-MXI-60530 |  | 3101-Z-6001, 3101-Z-6090 | 3101-MXI-60530 | Останов системы дробления резины, линия A | Shut down rubber breaking system line A | PLC signal | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6001B | PLC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 3 | Transfer from DCS to SIS | Rubber breaking system | ИД 2026 07 03 |  |  |  | 3101-P-LC-B01/3000-S-MC-B14 | PR01 | NH-DJYP3YP3 4x2x1.0 | 432 | 4x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire resistant | 3101-P-LC-B01 |  |  | - | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 24 | [12 empty] | Запись в БД произведена
4 | 3101 | 3101 | 3101-XZV-60509 | SDO0001-01 | 3101-XZV-60509 |  |  | 3101-XZY-60509 | Закрыть клапан пробки B в шредере для резины | Close the valve of plug B in rubber shredder | PLC signal | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6001B | PLC | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 2 | NEW | Rubber breaking system | ИД 2026 07 03 |  |  |  | 3101-S-JB-D112/3000-S-MC-B13 | PR05 | NH-KYJYP3 16x2.5 | 405 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D112 |  |  | 3101-XZY-60509/3101-S-JB-D112 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 11 | [12 empty] | Запись в БД произведена
5 | 3101 |  | 3101-MXI-60531 | SDO0001-01 | 3101-MXI-60531 |  | 3101-Z-6004, 3101-Z-6090 | 3101-MXI-60531 | Останов системы дробления резины, линия B | Shut down rubber breaking system line B | PLC signal | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6001B | PLC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤4 | [12 empty] | REV 3 | Transfer from DCS to SIS | Rubber breaking system | ИД 2026 07 03 |  |  |  | 3101-P-LC-B01/3000-S-MC-B14 | PR02 | NH-DJYP3YP3 4x2x1.0 | 432 | 4x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire resistant | 3101-P-LC-B01 |  |  | - | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 25 | [12 empty] | Запись в БД произведена
7 | 3101 | 3101 | 3101-AZIA-60001 | SAI1000-01R | 3101-AZIA-60001 |  | 3101-Z-6001 | 3101-AZT-60001 | Содержание O2 в отх. газе 3101-V-6001A | 3101-V-6001A Off Gas Oxygen Content | Paramagnetic oxygen analyzer | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | AIR-EP | Exd | SIS | I | 230V AC 4-wire external Power | SEE Power Supply List | 0 | 10 | vol% | 0 | 10 | vol% |  |  | 7 | 8 |  | vol% | REV 2 | Change instrument type | 3101-ACU-601 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B04 |  | A31 | A32 | 06 | - | A31-06 | - | A32-06 | - | 2 | [12 empty] | Запись в БД произведена
9 | 3101 | 3101 | 3101-XZV-60001 | SKLPD0021-00 | 3101-XZV-60001 |  |  | 3101-XZV-60001 | RS к V-6001A, блок. отсечки | RS to V-6001A Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
10 | 3101 | 3101 | 3101-XZV-60001 | SKLPD0021-00 | 3101-XZV-60001 |  | 3101-Z-6001, 3101-Z-6003, 3101-Z-6091 | 3101-XZY-60001 | RS к V-6001A, блок. отсечки | RS to V-6001A Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D112/3000-S-MC-B13 | PR01 | NH-KYJYP3 16x2.5 | 405 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D112 |  |  | 3101-XZY-60001/3101-S-JB-D112 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 7 | [12 empty] | Запись в БД произведена
11 | 3101 | 3101 | 3101-XZV-60001 | SKLPD0021-00 | 3101-XZV-60001 |  |  | 3101-XZZSC-60001 | RS к V-6001A, блок. отсечки (закрыт) | RS to V-6001A Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C111/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 405 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C111 |  |  | 3101-XZZSC-60001/3101-S-JB-C111 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 8 | [12 empty] | Запись в БД произведена
12 | 3101 | 3101 | 3101-XZV-60001 | SKLPD0021-00 | 3101-XZV-60001 |  |  | 3101-XZZSO-60001 | RS к V-6001A, блок. отсечки (открыт) | RS to V-6001A Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C111/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 405 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C111 |  |  | 3101-XZZSO-60001/3101-S-JB-C111 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 11 | [12 empty] | Запись в БД произведена
14 | 3101 | 3101 | 3101-XZV-60002 | SKLPD0021-00 | 3101-XZV-60002 |  |  | 3101-XZV-60002 | Выход V-6001A, блок. отсечки | 3101-V-6001A outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
15 | 3101 | 3101 | 3101-XZV-60002 | SKLPD0021-00 | 3101-XZV-60002 |  | 3101-Z-6003, 3101-Z-6014 | 3101-XZY-60002 | Выход V-6001A, блок. отсечки | 3101-V-6001A outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D106/3000-S-MC-B13 | PR01 | NH-KYJYP3 24x2.5 | 383 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D106 |  |  | 3101-XZY-60002/3101-S-JB-D106 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 0 | [12 empty] | Запись в БД произведена
16 | 3101 | 3101 | 3101-XZV-60002 | SKLPD0021-00 | 3101-XZV-60002 |  | 3101-Z-6002 | 3101-XZZSC-60002 | Выход V-6001A, блок. отсечки (закрыт) | 3101-V-6001A outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C104/3000-S-MC-B08 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C104 |  |  | 3101-XZZSC-60002/3101-S-JB-C104 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 0 | [12 empty] | Запись в БД произведена
17 | 3101 | 3101 | 3101-XZV-60002 | SKLPD0021-00 | 3101-XZV-60002 |  | 3101-Z-6002 | 3101-XZZSO-60002 | Выход V-6001A, блок. отсечки (открыт) | 3101-V-6001A outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C104/3000-S-MC-B08 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C104 |  |  | 3101-XZZSO-60002/3101-S-JB-C104 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 2 | [12 empty] | Запись в БД произведена
19 | 3101 | 3101 | 3101-LZIA-60002 | SAI1000-01R | 3101-LZIA-60002 |  | 3101-Z-6001, 3101-Z-6013 | 3101-LZT-60002 | Уровень в 3101-V-6001A | 3101-V-6001A Liquid level indication | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6000 | mm | 0 | 100 | % | 2,666667 | 13,66667 | 68,66667 | 79,66667 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3101-S-JB-C103/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C103 |  |  | 3101-LZT-60002/3101-S-JB-C103 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 0 | [12 empty] | Запись в БД произведена
21 | 3101 | 3101 | 3101-XZV-60007 | SKLPD0021-00 | 3101-XZV-60007 |  |  | 3101-XZV-60007 | Отс. клап. азота к 3101-V-6001A | nitrogen to 3101-V-6001A cut-off valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
22 | 3101 | 3101 | 3101-XZV-60007 | SKLPD0021-00 | 3101-XZV-60007 |  | 3101-Z-6001 | 3101-XZY-60007 | Отс. клап. азота к 3101-V-6001A | nitrogen to 3101-V-6001A cut-off valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D118/3000-S-MC-B10 | PR01 | NH-KYJYP3 16x2.5 | 370 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D118 |  |  | 3101-XZY-60007/3101-S-JB-D118 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 0 | [12 empty] | Запись в БД произведена
23 | 3101 | 3101 | 3101-XZV-60007 | SKLPD0021-00 | 3101-XZV-60007 |  |  | 3101-XZZSC-60007 | Отс. клап. азота к 3101-V-6001A (закрыт) | nitrogen to 3101-V-6001A cut-off valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C117/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 370 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C117 |  |  | 3101-XZZSC-60007/3101-S-JB-C117 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 14 | [12 empty] | Запись в БД произведена
24 | 3101 | 3101 | 3101-XZV-60007 | SKLPD0021-00 | 3101-XZV-60007 |  |  | 3101-XZZSO-60007 | Отс. клап. азота к 3101-V-6001A (открыт) | nitrogen to 3101-V-6001A cut-off valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C117/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 370 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C117 |  |  | 3101-XZZSO-60007/3101-S-JB-C117 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 17 | [12 empty] | Запись в БД произведена
26 | 3101 | 3101 | 3101-XZV-60011 | SKLPD0021-00 | 3101-XZV-60011 |  |  | 3101-XZV-60011 | Выход 3101-P-6001A/B, блок. отсечки | 3101-P-6001A/B outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
27 | 3101 | 3101 | 3101-XZV-60011 | SKLPD0021-00 | 3101-XZV-60011 |  | 3101-Z-6014 | 3101-XZY-60011 | Выход 3101-P-6001A/B, блок. отсечки | 3101-P-6001A/B outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D112/3000-S-MC-B13 | PR03 | NH-KYJYP3 16x2.5 | 405 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D112 |  |  | 3101-XZY-60011/3101-S-JB-D112 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 9 | [12 empty] | Запись в БД произведена
28 | 3101 | 3101 | 3101-XZV-60011 | SKLPD0021-00 | 3101-XZV-60011 |  |  | 3101-XZZSC-60011 | Выход 3101-P-6001A/B, блок. отсечки (закрыт) | 3101-P-6001A/B outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C111/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 405 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C111 |  |  | 3101-XZZSC-60011/3101-S-JB-C111 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 10 | [12 empty] | Запись в БД произведена
29 | 3101 | 3101 | 3101-XZV-60011 | SKLPD0021-00 | 3101-XZV-60011 |  |  | 3101-XZZSO-60011 | Выход 3101-P-6001A/B, блок. отсечки (открыт) | 3101-P-6001A/B outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C111/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 405 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C111 |  |  | 3101-XZZSO-60011/3101-S-JB-C111 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 13 | [12 empty] | Запись в БД произведена
31 | 2202 | 3101 | 3101-MXI-06001A | SDO0001-01 | 3101-MXI-06001A |  | 3101-Z-6002, 3101-Z-6003, 3101-Z-6005, 3101-Z-6006, 3101-Z-6008, 3101-Z-6010, 3101-Z-6013, 3101-Z-6014, 3101-Z-6015, 3101-Z-6090 | 3101-MXI-06001A | SIS стоп насоса подачи RS 3101-P-6001A | RS Delivery Pump 3101-P-6001A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6002 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 0 | [12 empty] | Запись в БД произведена
33 | 2202 | 3101 | 3101-MXI-16001A | SDO0001-01 | 3101-MXI-16001A |  | 3101-Z-6002, 3101-Z-6003, 3101-Z-6005, 3101-Z-6006, 3101-Z-6008, 3101-Z-6010, 3101-Z-6013, 3101-Z-6014, 3101-Z-6015, 3101-Z-6090 | 3101-MXI-16001A | SIS стоп насоса подачи RS 3101-P-6001B | RS Delivery Pump 3101-P-6001B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6002 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 10 | [12 empty] | Запись в БД произведена
35 | 2202 | 3101 | 3101-MXI-76001A | SDO0001-01 | 3101-MXI-76001A |  | 3101-Z-6090 | 3101-MXI-76001A | SIS стоп мешалки растворения резины 3101-AG-6001A | Rubber Dissolution Agitator 3101-AG-6001A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6002 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 28 | [12 empty] | Запись в БД произведена
37 | 3101 | 3101 | 3101-AZIA-60002 | SAI1000-01R | 3101-AZIA-60002 |  | 3101-Z-6004 | 3101-AZT-60002 | Содержание O2 в отх. газе 3101-V-6001B | 3101-V-6001B Off Gas Oxygen Content | Paramagnetic oxygen analyzer | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | AIR-EP | Exd | SIS | I | 230V AC 4-wire external Power | SEE Power Supply List | 0 | 10 | vol% | 0 | 10 | vol% |  |  | 7 | 9 |  | vol% | REV 2 | Change instrument type | 3101-ACU-602 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B04 |  | A31 | A32 | 06 | - | A31-06 | - | A32-06 | - | 3 | [12 empty] | Запись в БД произведена
39 | 3101 | 3101 | 3101-LZIA-60004 | SAI1000-01R | 3101-LZIA-60004 |  | 3101-Z-6004, 3101-Z-6015 | 3101-LZT-60004 | Уровень в 3101-V-6001B | 3101-V-6001B Liquid level indication | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6000 | mm | 0 | 100 | % | 2,666667 | 13,66667 | 68,66667 | 79,66667 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3101-S-JB-C103/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C103 |  |  | 3101-LZT-60004/3101-S-JB-C103 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 1 | [12 empty] | Запись в БД произведена
41 | 3101 | 3101 | 3101-TZIA-60003 | SAI1000-01R | 3101-TZIA-60003 |  | 3101-Z-6007 | 3101-TZT-60003 | Т на выходе трубного пучка 3101-E-6001, сигн. H (блок.) | 3101-E-6001 tubeside outlet temperature Indicator Interlock H alarm | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 100 | ℃ | -50 | 100 | ℃ |  |  | 50 | 55 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3101-S-JB-C116/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 370 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C116 |  |  | 3101-TZT-60003/3101-S-JB-C116 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 6 | [12 empty] | Запись в БД произведена
43 | 3101 | 3101 | 3101-XZV-60003 | SKLPD0021-00 | 3101-XZV-60003 |  |  | 3101-XZV-60003 | RS к V-6001B, блок. отсечки | RS to 3101-V-6001B Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
44 | 3101 | 3101 | 3101-XZV-60003 | SKLPD0021-00 | 3101-XZV-60003 |  | 3101-Z-6004, 3101-Z-6006, 3101-Z-6091 | 3101-XZY-60003 | RS к V-6001B, блок. отсечки | RS to 3101-V-6001B Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D112/3000-S-MC-B13 | PR02 | NH-KYJYP3 16x2.5 | 405 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D112 |  |  | 3101-XZY-60003/3101-S-JB-D112 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 8 | [12 empty] | Запись в БД произведена
45 | 3101 | 3101 | 3101-XZV-60003 | SKLPD0021-00 | 3101-XZV-60003 |  |  | 3101-XZZSC-60003 | RS к V-6001B, блок. отсечки (закрыт) | RS to 3101-V-6001B Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C111/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 405 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C111 |  |  | 3101-XZZSC-60003/3101-S-JB-C111 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 9 | [12 empty] | Запись в БД произведена
46 | 3101 | 3101 | 3101-XZV-60003 | SKLPD0021-00 | 3101-XZV-60003 |  |  | 3101-XZZSO-60003 | RS к V-6001B, блок. отсечки (открыт) | RS to 3101-V-6001B Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C111/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 405 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C111 |  |  | 3101-XZZSO-60003/3101-S-JB-C111 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 12 | [12 empty] | Запись в БД произведена
48 | 3101 | 3101 | 3101-XZV-60004 | SKLPD0021-00 | 3101-XZV-60004 |  |  | 3101-XZV-60004 | Выход V-6001B, блок. отсечки | 3101-V-6001B outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
49 | 3101 | 3101 | 3101-XZV-60004 | SKLPD0021-00 | 3101-XZV-60004 |  | 3101-Z-6006, 3101-Z-6014 | 3101-XZY-60004 | Выход V-6001B, блок. отсечки | 3101-V-6001B outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D106/3000-S-MC-B13 | PR02 | NH-KYJYP3 24x2.5 | 383 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D106 |  |  | 3101-XZY-60004/3101-S-JB-D106 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 1 | [12 empty] | Запись в БД произведена
50 | 3101 | 3101 | 3101-XZV-60004 | SKLPD0021-00 | 3101-XZV-60004 |  | 3101-Z-6005 | 3101-XZZSC-60004 | Выход V-6001B, блок. отсечки (закрыт) | 3101-V-6001B outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C104/3000-S-MC-B08 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C104 |  |  | 3101-XZZSC-60004/3101-S-JB-C104 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 1 | [12 empty] | Запись в БД произведена
51 | 3101 | 3101 | 3101-XZV-60004 | SKLPD0021-00 | 3101-XZV-60004 |  | 3101-Z-6005 | 3101-XZZSO-60004 | Выход V-6001B, блок. отсечки (открыт) | 3101-V-6001B outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C104/3000-S-MC-B08 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C104 |  |  | 3101-XZZSO-60004/3101-S-JB-C104 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 3 | [12 empty] | Запись в БД произведена
53 | 3101 | 3101 | 3101-XZV-60008 | SKLPD0021-00 | 3101-XZV-60008 |  |  | 3101-XZV-60008 | Отс. клап. азота к 3101-V-6001B | nitrogen to 3101-V-6001B cut-off valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
54 | 3101 | 3101 | 3101-XZV-60008 | SKLPD0021-00 | 3101-XZV-60008 |  | 3101-Z-6004 | 3101-XZY-60008 | Отс. клап. азота к 3101-V-6001B | nitrogen to 3101-V-6001B cut-off valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D118/3000-S-MC-B10 | PR02 | NH-KYJYP3 16x2.5 | 370 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D118 |  |  | 3101-XZY-60008/3101-S-JB-D118 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 1 | [12 empty] | Запись в БД произведена
55 | 3101 | 3101 | 3101-XZV-60008 | SKLPD0021-00 | 3101-XZV-60008 |  |  | 3101-XZZSC-60008 | Отс. клап. азота к 3101-V-6001B (закрыт) | nitrogen to 3101-V-6001B cut-off valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C117/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 370 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C117 |  |  | 3101-XZZSC-60008/3101-S-JB-C117 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 15 | [12 empty] | Запись в БД произведена
56 | 3101 | 3101 | 3101-XZV-60008 | SKLPD0021-00 | 3101-XZV-60008 |  |  | 3101-XZZSO-60008 | Отс. клап. азота к 3101-V-6001B (открыт) | nitrogen to 3101-V-6001B cut-off valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C117/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 370 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C117 |  |  | 3101-XZZSO-60008/3101-S-JB-C117 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 18 | [12 empty] | Запись в БД произведена
58 | 3101 | 3101 | 3101-XZV-60009 | SKLPD0021-00 | 3101-XZV-60009 |  |  | 3101-XZV-60009 | Отс. клап. рег. жидк. стирола в 3101-E-6001 | Adjust STY Liquid to 3101-E-6001 cut-off valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
59 | 3101 | 3101 | 3101-XZV-60009 | SKLPD0021-00 | 3101-XZV-60009 |  | 3101-Z-6001, 3101-Z-6003, 3101-Z-6004, 3101-Z-6006 | 3101-XZY-60009 | Отс. клап. рег. жидк. стирола в 3101-E-6001 | Adjust STY Liquid to 3101-E-6001 cut-off valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D118/3000-S-MC-B10 | PR03 | NH-KYJYP3 16x2.5 | 370 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D118 |  |  | 3101-XZY-60009/3101-S-JB-D118 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 2 | [12 empty] | Запись в БД произведена
60 | 3101 | 3101 | 3101-XZV-60009 | SKLPD0021-00 | 3101-XZV-60009 |  |  | 3101-XZZSC-60009 | Отс. клап. рег. жидк. стирола в 3101-E-6001 (закрыт) | Adjust STY Liquid to 3101-E-6001 cut-off valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C117/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 370 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C117 |  |  | 3101-XZZSC-60009/3101-S-JB-C117 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 16 | [12 empty] | Запись в БД произведена
61 | 3101 | 3101 | 3101-XZV-60009 | SKLPD0021-00 | 3101-XZV-60009 |  |  | 3101-XZZSO-60009 | Отс. клап. рег. жидк. стирола в 3101-E-6001 (открыт) | Adjust STY Liquid to 3101-E-6001 cut-off valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C117/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 370 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C117 |  |  | 3101-XZZSO-60009/3101-S-JB-C117 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 19 | [12 empty] | Запись в БД произведена
63 | 2202 | 3101 | 3101-MXI-86001A | SDO0001-01 | 3101-MXI-86001A |  | 3101-Z-6090 | 3101-MXI-86001A | SIS стоп мешалки растворения резины 3101-AG-6001B | Rubber Dissolution Agitator 3101-AG-6001B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6003 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 31 | [12 empty] | Запись в БД произведена
65 | 3101 | 3101 | 3101-LZIA-60006 | SAI1000-01R | 3101-LZIA-60006 |  | 3101-Z-6008, 3101-Z-6016 | 3101-LZT-60006 | Уровень в 3101-V-6002 | 3101-V-6002 Liquid level indication | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 10950 | mm | 0 | 100 | % | 14,66667 | 16,80365 | 70,22831 | 80,91324 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3101-S-JB-C103/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C103 |  |  | 3101-LZT-60006/3101-S-JB-C103 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 2 | [12 empty] | Запись в БД произведена
67 | 3101 | 3101 | 3101-PZIA-60006 | SAI1000-01R | 3101-PZIA-60006 |  | 3101-Z-6011 | 3101-PZT-60006 | Р на выходе 3101-F-6002A/B, сигн. HH (блок.) | 3101-F-6002A/B outlet pressure Indicator Interlock HH Alarm | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,4 | 1,45 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3101-S-JB-C116/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 370 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C116 |  |  | 3101-PZT-60006/3101-S-JB-C116 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 5 | [12 empty] | Запись в БД произведена
69 | 3101 | 3101 | 3101-XZV-60006 | SKLPD0021-00 | 3101-XZV-60006 |  |  | 3101-XZV-60006 | Выход V-6002, блок. отсечки | 3101-V-6002 outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
70 | 3101 | 3101 | 3101-XZV-60006 | SKLPD0021-00 | 3101-XZV-60006 |  | 3101-Z-6010, 3101-Z-6017 | 3101-XZY-60006 | Выход V-6002, блок. отсечки | 3101-V-6002 outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D106/3000-S-MC-B13 | PR03 | NH-KYJYP3 24x2.5 | 383 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D106 |  |  | 3101-XZY-60006/3101-S-JB-D106 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 2 | [12 empty] | Запись в БД произведена
71 | 3101 | 3101 | 3101-XZV-60006 | SKLPD0021-00 | 3101-XZV-60006 |  | 3101-Z-6009 | 3101-XZZSC-60006 | Выход V-6002, блок. отсечки (закрыт) | 3101-V-6002 outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C105/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C105 |  |  | 3101-XZZSC-60006/3101-S-JB-C105 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 0 | [12 empty] | Запись в БД произведена
72 | 3101 | 3101 | 3101-XZV-60006 | SKLPD0021-00 | 3101-XZV-60006 |  | 3101-Z-6009 | 3101-XZZSO-60006 | Выход V-6002, блок. отсечки (открыт) | 3101-V-6002 outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C105/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C105 |  |  | 3101-XZZSO-60006/3101-S-JB-C105 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 3 | [12 empty] | Запись в БД произведена
74 | 3101 | 3101 | 3101-XZV-60013 | SKLPD0021-00 | 3101-XZV-60013 |  |  | 3101-XZV-60013 | Выход 3101-P-6002, блок. отсечки | 3101-P-6002 outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
75 | 3101 | 3101 | 3101-XZV-60013 | SKLPD0021-00 | 3101-XZV-60013 |  | 3101-Z-6017 | 3101-XZY-60013 | Выход 3101-P-6002, блок. отсечки | 3101-P-6002 outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D106/3000-S-MC-B13 | PR04 | NH-KYJYP3 24x2.5 | 383 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D106 |  |  | 3101-XZY-60013/3101-S-JB-D106 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 3 | [12 empty] | Запись в БД произведена
76 | 3101 | 3101 | 3101-XZV-60013 | SKLPD0021-00 | 3101-XZV-60013 |  |  | 3101-XZZSC-60013 | Выход 3101-P-6002, блок. отсечки (закрыт) | 3101-P-6002 outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C105/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C105 |  |  | 3101-XZZSC-60013/3101-S-JB-C105 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 1 | [12 empty] | Запись в БД произведена
77 | 3101 | 3101 | 3101-XZV-60013 | SKLPD0021-00 | 3101-XZV-60013 |  |  | 3101-XZZSO-60013 | Выход 3101-P-6002, блок. отсечки (открыт) | 3101-P-6002 outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C105/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C105 |  |  | 3101-XZZSO-60013/3101-S-JB-C105 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 4 | [12 empty] | Запись в БД произведена
79 | 3101 | 3101 | 3101-XZV-60014 | SKLPD0021-00 | 3101-XZV-60014 |  |  | 3101-XZV-60014 | Выход 3101-P-6003A/B, блок. отсечки | 3101-P-6003A/B outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
80 | 3101 | 3101 | 3101-XZV-60014 | SKLPD0021-00 | 3101-XZV-60014 |  | 3101-Z-6017, 3101-Z-6091 | 3101-XZY-60014 | Выход 3101-P-6003A/B, блок. отсечки | 3101-P-6003A/B outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D106/3000-S-MC-B13 | PR05 | NH-KYJYP3 24x2.5 | 383 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D106 |  |  | 3101-XZY-60014/3101-S-JB-D106 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 4 | [12 empty] | Запись в БД произведена
81 | 3101 | 3101 | 3101-XZV-60014 | SKLPD0021-00 | 3101-XZV-60014 |  |  | 3101-XZZSC-60014 | Выход 3101-P-6003A/B, блок. отсечки (закрыт) | 3101-P-6003A/B outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C105/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C105 |  |  | 3101-XZZSC-60014/3101-S-JB-C105 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 2 | [12 empty] | Запись в БД произведена
82 | 3101 | 3101 | 3101-XZV-60014 | SKLPD0021-00 | 3101-XZV-60014 |  |  | 3101-XZZSO-60014 | Выход 3101-P-6003A/B, блок. отсечки (открыт) | 3101-P-6003A/B outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C105/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C105 |  |  | 3101-XZZSO-60014/3101-S-JB-C105 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 5 | [12 empty] | Запись в БД произведена
84 | 2202 | 3101 | 3101-MXI-06002A | SDO0001-01 | 3101-MXI-06002A |  | 3101-Z-6009, 3101-Z-6010, 3101-Z-6016, 3101-Z-6017, 3101-Z-6090 | 3101-MXI-06002A | SIS стоп цирк. насоса RS 3101-P-6002 | RS Circulation Pump 3101-P-6002 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6004 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 1 | [12 empty] | Запись в БД произведена
86 | 2202 | 3101 | 3101-MXI-06003A | SDO0001-01 | 3101-MXI-06003A |  | 3101-Z-6009, 3101-Z-6010, 3101-Z-6011, 3101-Z-6016, 3101-Z-6017, 3101-Z-6090 | 3101-MXI-06003A | SIS стоп насоса подачи RS 3101-P-6003A | RS Feed Pump 3101-P-6003A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6004 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 2 | [12 empty] | Запись в БД произведена
88 | 2202 | 3101 | 3101-MXI-16003A | SDO0001-01 | 3101-MXI-16003A |  | 3101-Z-6009,3101-Z-6010, 3101-Z-6011, 3101-Z-6016, 3101-Z-6017, 3101-Z-6090 | 3101-MXI-16003A | SIS стоп насоса подачи RS 3101-P-6003B | RS Feed Pump 3101-P-6003B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6004 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 11 | [12 empty] | Запись в БД произведена
90 | 2202 | 3101 | 3101-MXI-06004A | SDO0001-01 | 3101-MXI-06004A |  | 3101-Z-6090 | 3101-MXI-06004A | SIS стоп насоса полиизобутилена 3101-P-6004 | Polyisobutylene Pump 3101-P-6004 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6005 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 3 | [12 empty] | Запись в БД произведена
92 | 3104 | Сombined Title | 3101-LZIA-61002 | SAI1000-01R | 3101-LZIA-61002 |  | 3101-Z-6104 | 3101-LZT-61002 | Уровень в 3101-V-6102A, сигн. H, L | 3101-V-6102A Liquid level indication HL alarm | D/P Level Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1400 | mm | 0 | 100 | % | 13,17143 | 26,9 | 88,67857 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C296/3000-S-MC-B02 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C296 |  |  | 3101-LZT-61002/3104-S-JB-C296 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 3 | [12 empty] | Запись в БД произведена
94 | 3104 | Сombined Title | 3101-LZIA-61004 | SAI1000-01R | 3101-LZIA-61004 |  | 3101-Z-6105 | 3101-LZT-61004 | Уровень в 3101-V-6102B, сигн. H, L | 3101-V-6102B Liquid level indication HL alarm | D/P Level Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1400 | mm | 0 | 100 | % | 13,17143 | 26,9 | 88,67857 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C296/3000-S-MC-B02 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C296 |  |  | 3101-LZT-61004/3104-S-JB-C296 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 4 | [12 empty] | Запись в БД произведена
96 | 3104 | Сombined Title | 3101-XZV-61003 | SKLPD0021-00 | 3101-XZV-61003 |  |  | 3101-XZV-61003 | Вход 3101-P-6101A/B/C/D, блок. отсечки | 3101-P-6101A/B/C/D inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
97 | 3104 | Сombined Title | 3101-XZV-61003 | SKLPD0021-00 | 3101-XZV-61003 |  | 3101-Z-6106 | 3101-XZY-61003 | Вход 3101-P-6101A/B/C/D, блок. отсечки | 3101-P-6101A/B/C/D inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D286/3000-S-MC-B14 | PR01 | NH-KYJYP3 24x2.5 | 378 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D286 |  |  | 3101-XZY-61003/3104-S-JB-D286 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 20 | [12 empty] | Запись в БД произведена
98 | 3104 | Сombined Title | 3101-XZV-61003 | SKLPD0021-00 | 3101-XZV-61003 |  |  | 3101-XZZSC-61003 | Вход 3101-P-6101A/B/C/D, блок. отсечки (закрыт) | 3101-P-6101A/B/C/D inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3101-XZZSC-61003/3104-S-JB-C288 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 28 | [12 empty] | Запись в БД произведена
99 | 3104 | Сombined Title | 3101-XZV-61003 | SKLPD0021-00 | 3101-XZV-61003 |  |  | 3101-XZZSO-61003 | Вход 3101-P-6101A/B/C/D, блок. отсечки (открыт) | 3101-P-6101A/B/C/D inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3101-XZZSO-61003/3104-S-JB-C288 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 29 | [12 empty] | Запись в БД произведена
101 | 3104 | Сombined Title | 3101-XZV-61004 | SKLPD0021-00 | 3101-XZV-61004 |  |  | 3101-XZV-61004 | Выход 3101-P-6101A/B/C/D, блок. отсечки | 3101-P-6101A/B/C/D outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
102 | 3104 | Сombined Title | 3101-XZV-61004 | SKLPD0021-00 | 3101-XZV-61004 |  | 3101-Z-6106, 3104-Z-7291, 3102-Z-6291 | 3101-XZY-61004 | Выход 3101-P-6101A/B/C/D, блок. отсечки | 3101-P-6101A/B/C/D outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D287/3000-S-MC-B11 | PR01 | NH-KYJYP3 16x2.5 | 404 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D287 |  |  | 3101-XZY-61004/3104-S-JB-D287 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 9 | [12 empty] | Запись в БД произведена
103 | 3104 | Сombined Title | 3101-XZV-61004 | SKLPD0021-00 | 3101-XZV-61004 |  |  | 3101-XZZSC-61004 | Выход 3101-P-6101A/B/C/D, блок. отсечки (закрыт) | 3101-P-6101A/B/C/D outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSC-61004/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 4 | [12 empty] | Запись в БД произведена
104 | 3104 | Сombined Title | 3101-XZV-61004 | SKLPD0021-00 | 3101-XZV-61004 |  |  | 3101-XZZSO-61004 | Выход 3101-P-6101A/B/C/D, блок. отсечки (открыт) | 3101-P-6101A/B/C/D outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSO-61004/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 9 | [12 empty] | Запись в БД произведена
106 | 3104 | Сombined Title | 3101-XZV-61005 | SKLPD0021-00 | 3101-XZV-61005 |  |  | 3101-XZV-61005 | Выход 3101-P-6101A/B/C/D, блок. отсечки | 3101-P-6101A/B/C/D outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
107 | 3104 | Сombined Title | 3101-XZV-61005 | SKLPD0021-00 | 3101-XZV-61005 |  | 3101-Z-6106, 3104-Z-7291, 3102-Z-6291 | 3101-XZY-61005 | Выход 3101-P-6101A/B/C/D, блок. отсечки | 3101-P-6101A/B/C/D outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D287/3000-S-MC-B11 | PR02 | NH-KYJYP3 16x2.5 | 404 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D287 |  |  | 3101-XZY-61005/3104-S-JB-D287 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 10 | [12 empty] | Запись в БД произведена
108 | 3104 | Сombined Title | 3101-XZV-61005 | SKLPD0021-00 | 3101-XZV-61005 |  |  | 3101-XZZSC-61005 | Выход 3101-P-6101A/B/C/D, блок. отсечки (закрыт) | 3101-P-6101A/B/C/D outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSC-61005/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 5 | [12 empty] | Запись в БД произведена
109 | 3104 | Сombined Title | 3101-XZV-61005 | SKLPD0021-00 | 3101-XZV-61005 |  |  | 3101-XZZSO-61005 | Выход 3101-P-6101A/B/C/D, блок. отсечки (открыт) | 3101-P-6101A/B/C/D outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6102 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSO-61005/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 10 | [12 empty] | Запись в БД произведена
111 | 2202 | Сombined Title | 3101-MXI-76102A | SDO0001-01 | 3101-MXI-76102A |  | 3104-Z-7290 | 3101-MXI-76102A | SIS стоп мешалки емкости пригот. красителя 3101-AG-6102A | Dye Preparation Vessel Agitator 3101-AG-6102A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6102 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 29 | [12 empty] | Запись в БД произведена
113 | 2202 | Сombined Title | 3101-MXI-86102A | SDO0001-01 | 3101-MXI-86102A |  | 3104-Z-7290 | 3101-MXI-86102A | SIS стоп мешалки емкости пригот. красителя 3101-AG-6102B | Dye Preparation Vessel Agitator 3101-AG-6102B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6102 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 0 | [12 empty] | Запись в БД произведена
115 | 2202 | Сombined Title | 3101-MXI-06101A | SDO0001-01 | 3101-MXI-06101A |  | 3101-Z-6104, 3101-Z-6105, 3101-Z-6106, 3102-Z-6201, 3104-Z-7290 | 3101-MXI-06101A | SIS стоп насоса подачи красителя 3101-P-6101A | Dye Feed Pump 3101-P-6101A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6102 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 4 | [12 empty] | Запись в БД произведена
117 | 2202 | Сombined Title | 3101-MXI-16101A | SDO0001-01 | 3101-MXI-16101A |  | 3101-Z-6104, 3101-Z-6105, 3101-Z-6106, 3102-Z-6201, 3104-Z-7290 | 3101-MXI-16101A | SIS стоп насоса подачи красителя 3101-P-6101B | Dye Feed Pump 3101-P-6101B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6102 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 12 | [12 empty] | Запись в БД произведена
119 | 2202 | Сombined Title | 3101-MXI-26101A | SDO0001-01 | 3101-MXI-26101A |  | 3101-Z-6104, 3101-Z-6105, 3101-Z-6106, 3104-Z-7201, 3104-Z-7290 | 3101-MXI-26101A | SIS стоп насоса подачи красителя 3101-P-6101C | Dye Feed Pump 3101-P-6101C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6102 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 18 | [12 empty] | Запись в БД произведена
121 | 2202 | Сombined Title | 3101-MXI-36101A | SDO0001-01 | 3101-MXI-36101A |  | 3101-Z-6104, 3101-Z-6105, 3101-Z-6106, 3104-Z-7201, 3104-Z-7290 | 3101-MXI-36101A | SIS стоп насоса подачи красителя 3101-P-6101D | Dye Feed Pump 3101-P-6101D SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6102 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 23 | [12 empty] | Запись в БД произведена
123 | 3104 | Сombined Title | 3101-LZIA-61006 | SAI1000-01R | 3101-LZIA-61006 |  | 3101-Z-6107 | 3101-LZT-61006 | Уровень в 3101-V-6103A, сигн. H, L | 3101-V-6103A Liquid level indication HL alarm | D/P Level Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2700 | mm | 0 | 100 | % | 5,844444 | 12,47037 | 91,98148 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3101-LZT-61006/3104-S-JB-C249 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 6 | [12 empty] | Запись в БД произведена
125 | 3104 | Сombined Title | 3101-LZIA-61008 | SAI1000-01R | 3101-LZIA-61008 |  | 3101-Z-6108 | 3101-LZT-61008 | Уровень в 3101-V-6103B, сигн. H, L | 3101-V-6103B Liquid level indication HL alarm | D/P Level Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2700 | mm | 0 | 100 | % | 5,844444 | 12,47037 | 91,98148 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3101-LZT-61008/3104-S-JB-C261 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 13 | [12 empty] | Запись в БД произведена
127 | 3104 | Сombined Title | 3101-XZV-61006 | SKLPD0021-00 | 3101-XZV-61006 |  |  | 3101-XZV-61006 | Вход 3101-P-6102A/B/C/D, блок. отсечки | 3101-P-6102A/B/C/D inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
128 | 3104 | Сombined Title | 3101-XZV-61006 | SKLPD0021-00 | 3101-XZV-61006 |  | 3101-Z-6109 | 3101-XZY-61006 | Вход 3101-P-6102A/B/C/D, блок. отсечки | 3101-P-6102A/B/C/D inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D287/3000-S-MC-B11 | PR03 | NH-KYJYP3 16x2.5 | 404 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D287 |  |  | 3101-XZY-61006/3104-S-JB-D287 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 11 | [12 empty] | Запись в БД произведена
129 | 3104 | Сombined Title | 3101-XZV-61006 | SKLPD0021-00 | 3101-XZV-61006 |  |  | 3101-XZZSC-61006 | Вход 3101-P-6102A/B/C/D, блок. отсечки (закрыт) | 3101-P-6102A/B/C/D inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSC-61006/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 6 | [12 empty] | Запись в БД произведена
130 | 3104 | Сombined Title | 3101-XZV-61006 | SKLPD0021-00 | 3101-XZV-61006 |  |  | 3101-XZZSO-61006 | Вход 3101-P-6102A/B/C/D, блок. отсечки (открыт) | 3101-P-6102A/B/C/D inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSO-61006/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 11 | [12 empty] | Запись в БД произведена
132 | 3104 | Сombined Title | 3101-XZV-61007 | SKLPD0021-00 | 3101-XZV-61007 |  |  | 3101-XZV-61007 | Выход 3101-P-6102A/B, блок. отсечки | 3101-P-6102A/B outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
133 | 3104 | Сombined Title | 3101-XZV-61007 | SKLPD0021-00 | 3101-XZV-61007 |  | 3101-Z-6109, 3104-Z-7291, 3102-Z-6291 | 3101-XZY-61007 | Выход 3101-P-6102A/B, блок. отсечки | 3101-P-6102A/B outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D287/3000-S-MC-B11 | PR04 | NH-KYJYP3 16x2.5 | 404 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D287 |  |  | 3101-XZY-61007/3104-S-JB-D287 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 12 | [12 empty] | Запись в БД произведена
134 | 3104 | Сombined Title | 3101-XZV-61007 | SKLPD0021-00 | 3101-XZV-61007 |  |  | 3101-XZZSC-61007 | Выход 3101-P-6102A/B, блок. отсечки (закрыт) | 3101-P-6102A/B outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSC-61007/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 7 | [12 empty] | Запись в БД произведена
135 | 3104 | Сombined Title | 3101-XZV-61007 | SKLPD0021-00 | 3101-XZV-61007 |  |  | 3101-XZZSO-61007 | Выход 3101-P-6102A/B, блок. отсечки (открыт) | 3101-P-6102A/B outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSO-61007/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 12 | [12 empty] | Запись в БД произведена
137 | 3104 | Сombined Title | 3101-XZV-61008 | SKLPD0021-00 | 3101-XZV-61008 |  |  | 3101-XZV-61008 | Выход 3101-P-6102C/D, блок. отсечки | 3101-P-6102C/D outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
138 | 3104 | Сombined Title | 3101-XZV-61008 | SKLPD0021-00 | 3101-XZV-61008 |  | 3101-Z-6109, 3104-Z-7291, 3102-Z-6291 | 3101-XZY-61008 | Выход 3101-P-6102C/D, блок. отсечки | 3101-P-6102C/D outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D287/3000-S-MC-B11 | PR05 | NH-KYJYP3 16x2.5 | 404 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D287 |  |  | 3101-XZY-61008/3104-S-JB-D287 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 13 | [12 empty] | Запись в БД произведена
139 | 3104 | Сombined Title | 3101-XZV-61008 | SKLPD0021-00 | 3101-XZV-61008 |  |  | 3101-XZZSC-61008 | Выход 3101-P-6102C/D, блок. отсечки (закрыт) | 3101-P-6102C/D outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSC-61008/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 8 | [12 empty] | Запись в БД произведена
140 | 3104 | Сombined Title | 3101-XZV-61008 | SKLPD0021-00 | 3101-XZV-61008 |  |  | 3101-XZZSO-61008 | Выход 3101-P-6102C/D, блок. отсечки (открыт) | 3101-P-6102C/D outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6103 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C289/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 462 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C289 |  |  | 3101-XZZSO-61008/3104-S-JB-C289 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 13 | [12 empty] | Запись в БД произведена
142 | 2202 | Сombined Title | 3101-MXI-76103A | SDO0001-01 | 3101-MXI-76103A |  | 3104-Z-7290 | 3101-MXI-76103A | SIS стоп мешалки емкости пригот. RA 3101-AG-6103A | RA Preparation Vessel Agitator 3101-AG-6103A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6103 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 30 | [12 empty] | Запись в БД произведена
144 | 2202 | Сombined Title | 3101-MXI-86103A | SDO0001-01 | 3101-MXI-86103A |  | 3104-Z-7290 | 3101-MXI-86103A | SIS стоп мешалки емкости пригот. RA 3101-AG-6103B | RA Preparation Vessel Agitator 3101-AG-6103B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6103 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 1 | [12 empty] | Запись в БД произведена
146 | 2202 | Сombined Title | 3101-MXI-06102A | SDO0001-01 | 3101-MXI-06102A |  | 3101-Z-6107, 3101-Z-6108, 3101-Z-6109, 3102-Z-6201, 3104-Z-7290 | 3101-MXI-06102A | SIS стоп насоса подачи RA 3101-P-6102A | RA Feed Pump 3101-P-6102A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6103 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 5 | [12 empty] | Запись в БД произведена
148 | 2202 | Сombined Title | 3101-MXI-16102A | SDO0001-01 | 3101-MXI-16102A |  | 3101-Z-6107, 3101-Z-6108, 3101-Z-6109, 3102-Z-6201, 3104-Z-7290 | 3101-MXI-16102A | SIS стоп насоса подачи RA 3101-P-6102B | RA Feed Pump 3101-P-6102B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6103 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 13 | [12 empty] | Запись в БД произведена
150 | 2202 | Сombined Title | 3101-MXI-26102A | SDO0001-01 | 3101-MXI-26102A |  | 3101-Z-6107, 3101-Z-6108, 3101-Z-6109, 3104-Z-7201, 3104-Z-7290 | 3101-MXI-26102A | SIS стоп насоса подачи RA 3101-P-6102C | RA Feed Pump 3101-P-6102C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6103 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 19 | [12 empty] | Запись в БД произведена
152 | 2202 | Сombined Title | 3101-MXI-36102A | SDO0001-01 | 3101-MXI-36102A |  | 3101-Z-6107, 3101-Z-6108, 3101-Z-6109, 3104-Z-7201, 3104-Z-7290 | 3101-MXI-36102A | SIS стоп насоса подачи RA 3101-P-6102D | RA Feed Pump 3101-P-6102D SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6103 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 24 | [12 empty] | Запись в БД произведена
154 | 2202 | 3108 | 3108-MXI-06103A | SDO0001-01 | 3108-MXI-06103A |  | 3108-Z-6190 | 3108-MXI-06103A | SIS стоп насоса выдачи инициатора 3108-P-6103 | Initiator Discharge Pump 3108-P-6103 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6104 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 4 | [12 empty] | Запись в БД произведена
156 | 3108 | Сombined Title | 3101-LZIA-61013 | SAI1000-01R | 3101-LZIA-61013 |  | 3101-Z-6110 | 3101-LZT-61013 | Уровень в жирной трубе входа 3101-P-6104A/B, сигн. H, L | 3101-P-6104A/B Inlet fat pipe liquid level indicator HL alarm | D/P Level Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1300 | mm | 0 | 100 | % | 11,92308 | 23,46154 | 84,61538 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3108-S-JB-C424/3000-S-MC-B03 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 486 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C424 |  |  | 3101-LZT-61013/3108-S-JB-C424 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 4 | [12 empty] | Запись в БД произведена
158 | 3108 | Сombined Title | 3101-LZIA-61014 | SAI1000-01R | 3101-LZIA-61014 |  | 3101-Z-6111 | 3101-LZT-61014 | Уровень в жирной трубе входа 3101-P-6104C/D, сигн. H, L | 3101-P-6104C/D Inlet fat pipe liquid level indicator HL alarm | D/P Level Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1300 | mm | 0 | 100 | % | 11,92308 | 23,46154 | 84,61538 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3108-S-JB-C424/3000-S-MC-B03 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 486 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C424 |  |  | 3101-LZT-61014/3108-S-JB-C424 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 5 | [12 empty] | Запись в БД произведена
160 | 3108 | Сombined Title | 3101-XZV-61009 | SKLPD0021-00 | 3101-XZV-61009 |  |  | 3101-XZV-61009 | Вход 3101-P-6104A/B, блок. отсечки | 3101-P-6104A/B inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
161 | 3108 | Сombined Title | 3101-XZV-61009 | SKLPD0021-00 | 3101-XZV-61009 |  | 3101-Z-6112 | 3101-XZY-61009 | Вход 3101-P-6104A/B, блок. отсечки | 3101-P-6104A/B inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-D427/3000-S-MC-B11 | PR01 | NH-KYJYP3 16x2.5 | 486 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3108-S-JB-D427 |  |  | 3101-XZY-61009/3108-S-JB-D427 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 4 | [12 empty] | Запись в БД произведена
162 | 3108 | Сombined Title | 3101-XZV-61009 | SKLPD0021-00 | 3101-XZV-61009 |  |  | 3101-XZZSC-61009 | Вход 3101-P-6104A/B, блок. отсечки (закрыт) | 3101-P-6104A/B inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3101-XZZSC-61009/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 0 | [12 empty] | Запись в БД произведена
163 | 3108 | Сombined Title | 3101-XZV-61009 | SKLPD0021-00 | 3101-XZV-61009 |  |  | 3101-XZZSO-61009 | Вход 3101-P-6104A/B, блок. отсечки (открыт) | 3101-P-6104A/B inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3101-XZZSO-61009/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 4 | [12 empty] | Запись в БД произведена
165 | 3108 | Сombined Title | 3101-XZV-61010 | SKLPD0021-00 | 3101-XZV-61010 |  |  | 3101-XZV-61010 | Выход 3101-P-6104A/B, блок. отсечки | 3101-P-6104A/B outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
166 | 3108 | Сombined Title | 3101-XZV-61010 | SKLPD0021-00 | 3101-XZV-61010 |  | 3101-Z-6112, 3108-Z-6191 | 3101-XZY-61010 | Выход 3101-P-6104A/B, блок. отсечки | 3101-P-6104A/B outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-D427/3000-S-MC-B11 | PR02 | NH-KYJYP3 16x2.5 | 486 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3108-S-JB-D427 |  |  | 3101-XZY-61010/3108-S-JB-D427 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 5 | [12 empty] | Запись в БД произведена
167 | 3108 | Сombined Title | 3101-XZV-61010 | SKLPD0021-00 | 3101-XZV-61010 |  |  | 3101-XZZSC-61010 | Выход 3101-P-6104A/B, блок. отсечки (закрыт) | 3101-P-6104A/B outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3101-XZZSC-61010/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 1 | [12 empty] | Запись в БД произведена
168 | 3108 | Сombined Title | 3101-XZV-61010 | SKLPD0021-00 | 3101-XZV-61010 |  |  | 3101-XZZSO-61010 | Выход 3101-P-6104A/B, блок. отсечки (открыт) | 3101-P-6104A/B outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3101-XZZSO-61010/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 5 | [12 empty] | Запись в БД произведена
170 | 3108 | Сombined Title | 3101-XZV-61011 | SKLPD0021-00 | 3101-XZV-61011 |  |  | 3101-XZV-61011 | Вход 3101-P-6104C/D, блок. отсечки | 3101-P-6104C/D inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
171 | 3108 | Сombined Title | 3101-XZV-61011 | SKLPD0021-00 | 3101-XZV-61011 |  | 3101-Z-6113 | 3101-XZY-61011 | Вход 3101-P-6104C/D, блок. отсечки | 3101-P-6104C/D inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-D427/3000-S-MC-B11 | PR03 | NH-KYJYP3 16x2.5 | 486 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3108-S-JB-D427 |  |  | 3101-XZY-61011/3108-S-JB-D427 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 6 | [12 empty] | Запись в БД произведена
172 | 3108 | Сombined Title | 3101-XZV-61011 | SKLPD0021-00 | 3101-XZV-61011 |  |  | 3101-XZZSC-61011 | Вход 3101-P-6104C/D, блок. отсечки (закрыт) | 3101-P-6104C/D inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3101-XZZSC-61011/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 2 | [12 empty] | Запись в БД произведена
173 | 3108 | Сombined Title | 3101-XZV-61011 | SKLPD0021-00 | 3101-XZV-61011 |  |  | 3101-XZZSO-61011 | Вход 3101-P-6104C/D, блок. отсечки (открыт) | 3101-P-6104C/D inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3101-XZZSO-61011/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 6 | [12 empty] | Запись в БД произведена
175 | 3108 | Сombined Title | 3101-XZV-61012 | SKLPD0021-00 | 3101-XZV-61012 |  |  | 3101-XZV-61012 | Выход 3101-P-6104C/D, блок. отсечки | 3101-P-6104C/D outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
176 | 3108 | Сombined Title | 3101-XZV-61012 | SKLPD0021-00 | 3101-XZV-61012 |  | 3101-Z-6113, 3108-Z-6191 | 3101-XZY-61012 | Выход 3101-P-6104C/D, блок. отсечки | 3101-P-6104C/D outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-D427/3000-S-MC-B11 | PR04 | NH-KYJYP3 16x2.5 | 486 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3108-S-JB-D427 |  |  | 3101-XZY-61012/3108-S-JB-D427 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 7 | [12 empty] | Запись в БД произведена
177 | 3108 | Сombined Title | 3101-XZV-61012 | SKLPD0021-00 | 3101-XZV-61012 |  |  | 3101-XZZSC-61012 | Выход 3101-P-6104C/D, блок. отсечки (закрыт) | 3101-P-6104C/D outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3101-XZZSC-61012/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 3 | [12 empty] | Запись в БД произведена
178 | 3108 | Сombined Title | 3101-XZV-61012 | SKLPD0021-00 | 3101-XZV-61012 |  |  | 3101-XZZSO-61012 | Выход 3101-P-6104C/D, блок. отсечки (открыт) | 3101-P-6104C/D outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6105 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3101-XZZSO-61012/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 7 | [12 empty] | Запись в БД произведена
180 | 2202 | Сombined Title | 3101-MXI-06104A | SDO0001-01 | 3101-MXI-06104A |  | 3101-Z-6110, 3101-Z-6112, 3102-Z-6201, 3108-Z-6190 | 3101-MXI-06104A | SIS стоп насоса подачи инициатора 3101-P-6104A | Initiator Feed Pump 3101-P-6104A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6105 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 6 | [12 empty] | Запись в БД произведена
182 | 2202 | Сombined Title | 3101-MXI-16104A | SDO0001-01 | 3101-MXI-16104A |  | 3101-Z-6110, 3101-Z-6112, 3102-Z-6201, 3108-Z-6190 | 3101-MXI-16104A | SIS стоп насоса подачи инициатора 3101-P-6104B | Initiator Feed Pump 3101-P-6104B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6105 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 14 | [12 empty] | Запись в БД произведена
184 | 2202 | Сombined Title | 3101-MXI-26104A | SDO0001-01 | 3101-MXI-26104A |  | 3101-Z-6111, 3101-Z-6113, 3104-Z-7201, 3108-Z-6190 | 3101-MXI-26104A | SIS стоп насоса подачи инициатора 3101-P-6104C | Initiator Feed Pump 3101-P-6104C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6105 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 20 | [12 empty] | Запись в БД произведена
186 | 2202 | Сombined Title | 3101-MXI-36104A | SDO0001-01 | 3101-MXI-36104A |  | 3101-Z-6111, 3101-Z-6113, 3104-Z-7201, 3108-Z-6190 | 3101-MXI-36104A | SIS стоп насоса подачи инициатора 3101-P-6104D | Initiator Feed Pump 3101-P-6104D SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6105 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 25 | [12 empty] | Запись в БД произведена
188 | 3102 | 3101 | 3101-LZIA-61016 | SAI1000-01R | 3101-LZIA-61016 |  | 3101-Z-6101, 3101-Z-6114 | 3101-LZT-61016 | Уровень в 3101-V-6105, сигн. HH (блок.) | 3101-V-6105 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6106 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2800 | mm | 0 | 100 | % | 7,5 | 13,57143 | 80,35714 | 92,5 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C179/3000-S-MC-B02 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C179 |  |  | 3101-LZT-61016/3102-S-JB-C179 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 0 | [12 empty] | Запись в БД произведена
190 | 3102 | 3101 | 3101-XZV-61001 | SKLPD0021-00 | 3101-XZV-61001 |  |  | 3101-XZV-61001 | EB к V-6105, блок. отсечки | EB to 3101-V-6105 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6106 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
191 | 3102 | 3101 | 3101-XZV-61001 | SKLPD0021-00 | 3101-XZV-61001 |  | 3101-Z-6101, 3101-Z-6091 | 3101-XZY-61001 | EB к V-6105, блок. отсечки | EB to 3101-V-6105 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6106 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR07 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3101-XZY-61001/3102-S-JB-D165 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 31 | [12 empty] | Запись в БД произведена
192 | 3102 | 3101 | 3101-XZV-61001 | SKLPD0021-00 | 3101-XZV-61001 |  |  | 3101-XZZSC-61001 | EB к V-6105, блок. отсечки (закрыт) | EB to 3101-V-6105 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6106 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C174/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 450 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C174 |  |  | 3101-XZZSC-61001/3102-S-JB-C174 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 18 | [12 empty] | Запись в БД произведена
193 | 3102 | 3101 | 3101-XZV-61001 | SKLPD0021-00 | 3101-XZV-61001 |  |  | 3101-XZZSO-61001 | EB к V-6105, блок. отсечки (открыт) | EB to 3101-V-6105 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6106 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C174/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 450 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C174 |  |  | 3101-XZZSO-61001/3102-S-JB-C174 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 19 | [12 empty] | Запись в БД произведена
195 | 3102 | Сombined Title | 3101-XZV-61013 | SKLPD0021-00 | 3101-XZV-61013 |  |  | 3101-XZV-61013 | Вход 3101-P-6106A/B/C/D, блок. отсечки | 3101-P-6106A/B/C/D inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
196 | 3102 | Сombined Title | 3101-XZV-61013 | SKLPD0021-00 | 3101-XZV-61013 |  | 3101-Z-6115 | 3101-XZY-61013 | Вход 3101-P-6106A/B/C/D, блок. отсечки | 3101-P-6106A/B/C/D inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR01 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3101-XZY-61013/3102-S-JB-D157 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 16 | [12 empty] | Запись в БД произведена
197 | 3102 | Сombined Title | 3101-XZV-61013 | SKLPD0021-00 | 3101-XZV-61013 |  |  | 3101-XZZSC-61013 | Вход 3101-P-6106A/B/C/D, блок. отсечки (закрыт) | 3101-P-6106A/B/C/D inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSC-61013/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 0 | [12 empty] | Запись в БД произведена
198 | 3102 | Сombined Title | 3101-XZV-61013 | SKLPD0021-00 | 3101-XZV-61013 |  |  | 3101-XZZSO-61013 | Вход 3101-P-6106A/B/C/D, блок. отсечки (открыт) | 3101-P-6106A/B/C/D inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSO-61013/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 6 | [12 empty] | Запись в БД произведена
200 | 3102 | Сombined Title | 3101-XZV-61014 | SKLPD0021-00 | 3101-XZV-61014 |  |  | 3101-XZV-61014 | Выход 3101-P-6106A/B, блок. отсечки | 3101-P-6106A/B outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
201 | 3102 | Сombined Title | 3101-XZV-61014 | SKLPD0021-00 | 3101-XZV-61014 |  | 3101-Z-6115 | 3101-XZY-61014 | Выход 3101-P-6106A/B, блок. отсечки | 3101-P-6106A/B outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR02 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3101-XZY-61014/3102-S-JB-D157 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 17 | [12 empty] | Запись в БД произведена
202 | 3102 | Сombined Title | 3101-XZV-61014 | SKLPD0021-00 | 3101-XZV-61014 |  |  | 3101-XZZSC-61014 | Выход 3101-P-6106A/B, блок. отсечки (закрыт) | 3101-P-6106A/B outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSC-61014/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 1 | [12 empty] | Запись в БД произведена
203 | 3102 | Сombined Title | 3101-XZV-61014 | SKLPD0021-00 | 3101-XZV-61014 |  |  | 3101-XZZSO-61014 | Выход 3101-P-6106A/B, блок. отсечки (открыт) | 3101-P-6106A/B outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSO-61014/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 7 | [12 empty] | Запись в БД произведена
205 | 3102 | Сombined Title | 3101-XZV-61015 | SKLPD0021-00 | 3101-XZV-61015 |  |  | 3101-XZV-61015 | Выход 3101-P-6106C/D, блок. отсечки | 3101-P-6106C/D outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
206 | 3102 | Сombined Title | 3101-XZV-61015 | SKLPD0021-00 | 3101-XZV-61015 |  | 3101-Z-6115 | 3101-XZY-61015 | Выход 3101-P-6106C/D, блок. отсечки | 3101-P-6106C/D outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR08 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3101-XZY-61015/3102-S-JB-D157 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 18 | [12 empty] | Запись в БД произведена
207 | 3102 | Сombined Title | 3101-XZV-61015 | SKLPD0021-00 | 3101-XZV-61015 |  |  | 3101-XZZSC-61015 | Выход 3101-P-6106C/D, блок. отсечки (закрыт) | 3101-P-6106C/D outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSC-61015/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 2 | [12 empty] | Запись в БД произведена
208 | 3102 | Сombined Title | 3101-XZV-61015 | SKLPD0021-00 | 3101-XZV-61015 |  |  | 3101-XZZSO-61015 | Выход 3101-P-6106C/D, блок. отсечки (открыт) | 3101-P-6106C/D outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6106 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSO-61015/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 8 | [12 empty] | Запись в БД произведена
210 | 2202 | 3101 | 3101-MXI-06106A | SDO0001-01 | 3101-MXI-06106A |  | 3101-Z-6114, 3101-Z-6115,3102-Z-6201, 3102-Z-6290 | 3101-MXI-06106A | SIS стоп насоса подачи EB 3101-P-6106A | EB Feed Pump 3101-P-6106A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6106 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 7 | [12 empty] | Запись в БД произведена
212 | 2202 | 3101 | 3101-MXI-16106A | SDO0001-01 | 3101-MXI-16106A |  | 3101-Z-6114, 3101-Z-6115, 3102-Z-6201, 3102-Z-6290 | 3101-MXI-16106A | SIS стоп насоса подачи EB 3101-P-6106B | EB Feed Pump 3101-P-6106B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6106 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 15 | [12 empty] | Запись в БД произведена
214 | 2202 | 3101 | 3101-MXI-26106A | SDO0001-01 | 3101-MXI-26106A |  | 3101-Z-6114, 3101-Z-6115, 3104-Z-7201, 3102-Z-6290 | 3101-MXI-26106A | SIS стоп насоса подачи EB 3101-P-6106C | EB Feed Pump 3101-P-6106C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6106 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 21 | [12 empty] | Запись в БД произведена
216 | 2202 | 3101 | 3101-MXI-36106A | SDO0001-01 | 3101-MXI-36106A |  | 3101-Z-6114, 3101-Z-6115, 3104-Z-7201, 3102-Z-6290 | 3101-MXI-36106A | SIS стоп насоса подачи EB 3101-P-6106D | EB Feed Pump 3101-P-6106D SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6106 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 26 | [12 empty] | Запись в БД произведена
218 | 3102 | 3109 | 3101-LZIA-61018 | SAI1000-01R | 3101-LZIA-61018 |  | 3101-Z-6102, 3101-Z-6116 | 3101-LZT-61018 | Уровень в 3101-V-6106, сигн. HH (блок.) | 3101-V-6106 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6107 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2800 | mm | 0 | 100 | % | 7,5 | 13,57143 | 80,35714 | 92,5 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C179/3000-S-MC-B02 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C179 |  |  | 3101-LZT-61018/3102-S-JB-C179 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 1 | [12 empty] | Запись в БД произведена
220 | 3102 | 3109 | 3109-XZV-61002 | SKLPD0021-00 | 3109-XZV-61002 |  |  | 3109-XZV-61002 | МО к V-6106, блок. отсечки | MO to 3101-V-6106 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6107 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
221 | 3102 | 3109 | 3109-XZV-61002 | SKLPD0021-00 | 3109-XZV-61002 |  | 3101-Z-6102, 3101-Z-6091 | 3109-XZY-61002 | МО к V-6106, блок. отсечки | MO to 3101-V-6106 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6107 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D183/3000-S-MC-B11 | PR05 | NH-KYJYP3 16x2.5 | 434 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D183 |  |  | 3109-XZY-61002/3102-S-JB-D183 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 0 | [12 empty] | Запись в БД произведена
222 | 3102 | 3109 | 3109-XZV-61002 | SKLPD0021-00 | 3109-XZV-61002 |  |  | 3109-XZZSC-61002 | МО к V-6106, блок. отсечки (закрыт) | MO to 3101-V-6106 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6107 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3109-XZZSC-61002/3102-S-JB-C180 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 20 | [12 empty] | Запись в БД произведена
223 | 3102 | 3109 | 3109-XZV-61002 | SKLPD0021-00 | 3109-XZV-61002 |  |  | 3109-XZZSO-61002 | МО к V-6106, блок. отсечки (открыт) | MO to 3101-V-6106 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6107 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3109-XZZSO-61002/3102-S-JB-C180 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 21 | [12 empty] | Запись в БД произведена
225 | 3102 | Сombined Title | 3101-XZV-61016 | SKLPD0021-00 | 3101-XZV-61016 |  |  | 3101-XZV-61016 | Вход 3101-P-6107A/B/C/D, блок. отсечки | 3101-P-6107A/B/C/D inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
226 | 3102 | Сombined Title | 3101-XZV-61016 | SKLPD0021-00 | 3101-XZV-61016 |  | 3101-Z-6117 | 3101-XZY-61016 | Вход 3101-P-6107A/B/C/D, блок. отсечки | 3101-P-6107A/B/C/D inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR06 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3101-XZY-61016/3102-S-JB-D157 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 19 | [12 empty] | Запись в БД произведена
227 | 3102 | Сombined Title | 3101-XZV-61016 | SKLPD0021-00 | 3101-XZV-61016 |  |  | 3101-XZZSC-61016 | Вход 3101-P-6107A/B/C/D, блок. отсечки (закрыт) | 3101-P-6107A/B/C/D inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSC-61016/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 3 | [12 empty] | Запись в БД произведена
228 | 3102 | Сombined Title | 3101-XZV-61016 | SKLPD0021-00 | 3101-XZV-61016 |  |  | 3101-XZZSO-61016 | Вход 3101-P-6107A/B/C/D, блок. отсечки (открыт) | 3101-P-6107A/B/C/D inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSO-61016/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 9 | [12 empty] | Запись в БД произведена
230 | 3102 | Сombined Title | 3101-XZV-61017 | SKLPD0021-00 | 3101-XZV-61017 |  |  | 3101-XZV-61017 | Выход 3101-P-6107A/B, блок. отсечки | 3101-P-6107A/B outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
231 | 3102 | Сombined Title | 3101-XZV-61017 | SKLPD0021-00 | 3101-XZV-61017 |  | 3101-Z-6117 | 3101-XZY-61017 | Выход 3101-P-6107A/B, блок. отсечки | 3101-P-6107A/B outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR09 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3101-XZY-61017/3102-S-JB-D157 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 20 | [12 empty] | Запись в БД произведена
232 | 3102 | Сombined Title | 3101-XZV-61017 | SKLPD0021-00 | 3101-XZV-61017 |  |  | 3101-XZZSC-61017 | Выход 3101-P-6107A/B, блок. отсечки (закрыт) | 3101-P-6107A/B outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSC-61017/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 4 | [12 empty] | Запись в БД произведена
233 | 3102 | Сombined Title | 3101-XZV-61017 | SKLPD0021-00 | 3101-XZV-61017 |  |  | 3101-XZZSO-61017 | Выход 3101-P-6107A/B, блок. отсечки (открыт) | 3101-P-6107A/B outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSO-61017/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 10 | [12 empty] | Запись в БД произведена
235 | 3102 | Сombined Title | 3101-XZV-61018 | SKLPD0021-00 | 3101-XZV-61018 |  |  | 3101-XZV-61018 | Выход 3101-P-6107C/D, блок. отсечки | 3101-P-6107C/D outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
236 | 3102 | Сombined Title | 3101-XZV-61018 | SKLPD0021-00 | 3101-XZV-61018 |  | 3101-Z-6117 | 3101-XZY-61018 | Выход 3101-P-6107C/D, блок. отсечки | 3101-P-6107C/D outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR10 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3101-XZY-61018/3102-S-JB-D157 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 21 | [12 empty] | Запись в БД произведена
237 | 3102 | Сombined Title | 3101-XZV-61018 | SKLPD0021-00 | 3101-XZV-61018 |  |  | 3101-XZZSC-61018 | Выход 3101-P-6107C/D, блок. отсечки (закрыт) | 3101-P-6107C/D outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSC-61018/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 5 | [12 empty] | Запись в БД произведена
238 | 3102 | Сombined Title | 3101-XZV-61018 | SKLPD0021-00 | 3101-XZV-61018 |  |  | 3101-XZZSO-61018 | Выход 3101-P-6107C/D, блок. отсечки (открыт) | 3101-P-6107C/D outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6107 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C155/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 427 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C155 |  |  | 3101-XZZSO-61018/3102-S-JB-C155 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 11 | [12 empty] | Запись в БД произведена
240 | 2202 | Сombined Title | 3101-MXI-06107A | SDO0001-01 | 3101-MXI-06107A |  | 3101-Z-6116, 3101-Z-6117, 3102-Z-6201, 3102-Z-6290 | 3101-MXI-06107A | SIS стоп насоса подачи МО 3101-P-6107A | MO Feed Pump 3101-P-6107A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6107 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 8 | [12 empty] | Запись в БД произведена
242 | 2202 | Сombined Title | 3101-MXI-16107A | SDO0001-01 | 3101-MXI-16107A |  | 3101-Z-6116, 3101-Z-6117, 3102-Z-6201, 3102-Z-6290 | 3101-MXI-16107A | SIS стоп насоса подачи МО 3101-P-6107B | MO Feed Pump 3101-P-6107B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6107 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 16 | [12 empty] | Запись в БД произведена
244 | 2202 | Сombined Title | 3101-MXI-26107A | SDO0001-01 | 3101-MXI-26107A |  | 3101-Z-6116, 3101-Z-6117, 3104-Z-7201, 3102-Z-6290 | 3101-MXI-26107A | SIS стоп насоса подачи МО 3101-P-6107C | MO Feed Pump 3101-P-6107C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6107 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 22 | [12 empty] | Запись в БД произведена
246 | 2202 | Сombined Title | 3101-MXI-36107A | SDO0001-01 | 3101-MXI-36107A |  | 3101-Z-6116, 3101-Z-6117, 3104-Z-7201, 3102-Z-6290 | 3101-MXI-36107A | SIS стоп насоса подачи МО 3101-P-6107D | MO Feed Pump 3101-P-6107D SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6107 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 27 | [12 empty] | Запись в БД произведена
248 | 3108 | Сombined Title | 3102-LZIA-61102 | SAI1000-01R | 3102-LZIA-61102 |  | 3108-Z-6118 | 3102-LZT-61102 | Уровень в 3108-V-6107, сигн. H, L | 3108-V-6107 Liquid level indication HL alarm | D/P Level Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6108 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1400 | mm | 0 | 100 | % | 11,42857 | 17,85714 | 82,14286 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3108-S-JB-C424/3000-S-MC-B03 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 486 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C424 |  |  | 3102-LZT-61102/3108-S-JB-C424 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 6 | [12 empty] | Запись в БД произведена
250 | 3108 | Сombined Title | 3108-XZV-61019 | SKLPD0021-00 | 3108-XZV-61019 |  |  | 3108-XZV-61019 | Вход 3108-P-6105A/B, блок. отсечки | 3108-P-6105A/B inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6108 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
251 | 3108 | Сombined Title | 3108-XZV-61019 | SKLPD0021-00 | 3108-XZV-61019 |  | 3108-Z-6119 | 3108-XZY-61019 | Вход 3108-P-6105A/B, блок. отсечки | 3108-P-6105A/B inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6108 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-D427/3000-S-MC-B11 | PR05 | NH-KYJYP3 16x2.5 | 486 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3108-S-JB-D427 |  |  | 3108-XZY-61019/3108-S-JB-D427 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 8 | [12 empty] | Запись в БД произведена
252 | 3108 | Сombined Title | 3108-XZV-61019 | SKLPD0021-00 | 3108-XZV-61019 |  |  | 3108-XZZSC-61019 | Вход 3108-P-6105A/B, блок. отсечки (закрыт) | 3108-P-6105A/B inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6108 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3108-XZZSC-61019/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 8 | [12 empty] | Запись в БД произведена
253 | 3108 | Сombined Title | 3108-XZV-61019 | SKLPD0021-00 | 3108-XZV-61019 |  |  | 3108-XZZSO-61019 | Вход 3108-P-6105A/B, блок. отсечки (открыт) | 3108-P-6105A/B inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6108 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3108-XZZSO-61019/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 10 | [12 empty] | Запись в БД произведена
255 | 3108 | Сombined Title | 3108-XZV-61020 | SKLPD0021-00 | 3108-XZV-61020 |  |  | 3108-XZV-61020 | Выход 3108-P-6105A/B, блок. отсечки | 3108-P-6105A/B outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6108 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
256 | 3108 | Сombined Title | 3108-XZV-61020 | SKLPD0021-00 | 3108-XZV-61020 |  | 3108-Z-6119, 3108-Z-6191 | 3108-XZY-61020 | Выход 3108-P-6105A/B, блок. отсечки | 3108-P-6105A/B outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6108 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-D427/3000-S-MC-B11 | PR06 | NH-KYJYP3 16x2.5 | 486 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3108-S-JB-D427 |  |  | 3108-XZY-61020/3108-S-JB-D427 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 9 | [12 empty] | Запись в БД произведена
257 | 3108 | Сombined Title | 3108-XZV-61020 | SKLPD0021-00 | 3108-XZV-61020 |  |  | 3108-XZZSC-61020 | Выход 3108-P-6105A/B, блок. отсечки (закрыт) | 3108-P-6105A/B outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6108 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3108-XZZSC-61020/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 9 | [12 empty] | Запись в БД произведена
258 | 3108 | Сombined Title | 3108-XZV-61020 | SKLPD0021-00 | 3108-XZV-61020 |  |  | 3108-XZZSO-61020 | Выход 3108-P-6105A/B, блок. отсечки (открыт) | 3108-P-6105A/B outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6108 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C425/3000-S-MC-B09 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 486 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C425 |  |  | 3108-XZZSO-61020/3108-S-JB-C425 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 11 | [12 empty] | Запись в БД произведена
260 | 2202 | Сombined Title | 3108-MXI-06105A | SDO0001-01 | 3108-MXI-06105A |  | 3108-Z-6118, 3108-Z-6119, 3102-Z-6201, 3104-Z-7201, 3108-Z-6190 | 3108-MXI-06105A | SIS стоп насоса подачи меркаптана 3108-P-6105A | Mercaptan Feed Pump 3108-P-6105A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6108 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 5 | [12 empty] | Запись в БД произведена
262 | 2202 | Сombined Title | 3108-MXI-16105A | SDO0001-01 | 3108-MXI-16105A |  | 3108-Z-6118, 3108-Z-6119, 3102-Z-6201, 3104-Z-7201, 3108-Z-6190 | 3108-MXI-16105A | SIS стоп насоса подачи меркаптана 3108-P-6105B | Mercaptan Feed Pump 3108-P-6105B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6108 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 6 | [12 empty] | Запись в БД произведена
264 | 3107 | 3109 | 3101-LZIA-61802 | SAI1000-01R | 3101-LZIA-61802 |  | 3101-Z-6103, 3101-Z-6120 | 3101-LZT-61802 | Уровень в 3101-V-6108, сигн. HH (блок.) | 3101-V-6108 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6109 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2800 | mm | 0 | 100 | % | 7,5 | 13,57143 | 80,35714 | 92,5 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C410/3000-S-MC-B03 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 436 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C410 |  |  | 3101-LZT-61802/3107-S-JB-C410 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 3 | [12 empty] | Запись в БД произведена
266 | 3107 | 3109 | 3109-XZV-61801 | SKLPD0021-00 | 3109-XZV-61801 |  |  | 3109-XZV-61801 | МО к V-6108, блок. отсечки | MO to 3101-V-6108 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6109 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
267 | 3107 | 3109 | 3109-XZV-61801 | SKLPD0021-00 | 3109-XZV-61801 |  | 3101-Z-6103, 3101-Z-6091 | 3109-XZY-61801 | МО к V-6108, блок. отсечки | MO to 3101-V-6108 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6109 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-D413/3000-S-MC-B14 | PR04 | NH-KYJYP3 16x2.5 | 436 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D413 |  |  | 3109-XZY-61801/3107-S-JB-D413 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 11 | [12 empty] | Запись в БД произведена
268 | 3107 | 3109 | 3109-XZV-61801 | SKLPD0021-00 | 3109-XZV-61801 |  |  | 3109-XZZSC-61801 | МО к V-6108, блок. отсечки (закрыт) | MO to 3101-V-6108 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6109 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3109-XZZSC-61801/3107-S-JB-C411 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 12 | [12 empty] | Запись в БД произведена
269 | 3107 | 3109 | 3109-XZV-61801 | SKLPD0021-00 | 3109-XZV-61801 |  |  | 3109-XZZSO-61801 | МО к V-6108, блок. отсечки (открыт) | MO to 3101-V-6108 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6109 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3109-XZZSO-61801/3107-S-JB-C411 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 13 | [12 empty] | Запись в БД произведена
271 | 3107 | Сombined Title | 3101-XZV-61021 | SKLPD0021-00 | 3101-XZV-61021 |  |  | 3101-XZV-61021 | Вход 3101-P-6108A/B, блок. отсечки | 3101-P-6108A/B inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6109 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
272 | 3107 | Сombined Title | 3101-XZV-61021 | SKLPD0021-00 | 3101-XZV-61021 |  | 3101-Z-6121 | 3101-XZY-61021 | Вход 3101-P-6108A/B, блок. отсечки | 3101-P-6108A/B inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6109 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-D413/3000-S-MC-B14 | PR01 | NH-KYJYP3 16x2.5 | 436 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D413 |  |  | 3101-XZY-61021/3107-S-JB-D413 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 16 | [12 empty] | Запись в БД произведена
273 | 3107 | Сombined Title | 3101-XZV-61021 | SKLPD0021-00 | 3101-XZV-61021 |  |  | 3101-XZZSC-61021 | Вход 3101-P-6108A/B, блок. отсечки (закрыт) | 3101-P-6108A/B inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6109 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3101-XZZSC-61021/3107-S-JB-C411 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 5 | [12 empty] | Запись в БД произведена
274 | 3107 | Сombined Title | 3101-XZV-61021 | SKLPD0021-00 | 3101-XZV-61021 |  |  | 3101-XZZSO-61021 | Вход 3101-P-6108A/B, блок. отсечки (открыт) | 3101-P-6108A/B inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6109 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3101-XZZSO-61021/3107-S-JB-C411 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 6 | [12 empty] | Запись в БД произведена
276 | 3107 | Сombined Title | 3101-XZV-61022 | SKLPD0021-00 | 3101-XZV-61022 |  |  | 3101-XZV-61022 | Выход 3101-P-6108A/B, блок. отсечки | 3101-P-6108A/B outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6109 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
277 | 3107 | Сombined Title | 3101-XZV-61022 | SKLPD0021-00 | 3101-XZV-61022 |  | 3101-Z-6121 | 3101-XZY-61022 | Выход 3101-P-6108A/B, блок. отсечки | 3101-P-6108A/B outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6109 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-D407/3000-S-MC-B13 | PR01 | NH-KYJYP3 16x2.5 | 447 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D407 |  |  | 3101-XZY-61022/3107-S-JB-D407 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 29 | [12 empty] | Запись в БД произведена
278 | 3107 | Сombined Title | 3101-XZV-61022 | SKLPD0021-00 | 3101-XZV-61022 |  |  | 3101-XZZSC-61022 | Выход 3101-P-6108A/B, блок. отсечки (закрыт) | 3101-P-6108A/B outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6109 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C404/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 447 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C404 |  |  | 3101-XZZSC-61022/3107-S-JB-C404 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 14 | [12 empty] | Запись в БД произведена
279 | 3107 | Сombined Title | 3101-XZV-61022 | SKLPD0021-00 | 3101-XZV-61022 |  |  | 3101-XZZSO-61022 | Выход 3101-P-6108A/B, блок. отсечки (открыт) | 3101-P-6108A/B outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6109 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C404/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 447 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C404 |  |  | 3101-XZZSO-61022/3107-S-JB-C404 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 15 | [12 empty] | Запись в БД произведена
281 | 2202 | Сombined Title | 3101-MXI-06108A | SDO0001-01 | 3101-MXI-06108A |  | 3101-Z-6120, 3101-Z-6121, 3102-Z-6201, 3104-Z-7201, 3107-Z-6490 | 3101-MXI-06108A | SIS стоп насоса подачи спец. МО 3101-P-6108A | Special MO Feed Pump 3101-P-6108A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6109 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 9 | [12 empty] | Запись в БД произведена
283 | 2202 | Сombined Title | 3101-MXI-16108A | SDO0001-01 | 3101-MXI-16108A |  | 3101-Z-6120, 3101-Z-6121, 3102-Z-6201, 3104-Z-7201, 3107-Z-6490 | 3101-MXI-16108A | SIS стоп насоса подачи спец. МО 3101-P-6108B | Special MO Feed Pump 3101-P-6108B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6109 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 02 | 03 | A70-02 | A70-03 | A71-02 | A71-03 | 17 | [12 empty] | Запись в БД произведена
285 | 3102 | Сombined Title | 3102-FZIA-62004 | SAI1000-01R | 3102-FZIA-62004 |  | 3102-Z-6201 | 3102-FZT-62004 | Рег. расхода от 3102-MX-6201 к 3102-E-6201 | 3102-MX-6201 to 3102-E-6201 flow control | CORIOLIS FLOW TRANSMITTER | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | AIR-EP | Exd | SIS | I | 24V DC 4-wire external Power | 20 | 0 | 30000 | kg/h | 0 | 30000 | kg/h | 4000 | 4500 |  |  |  | kg/h |  |  |  | ИД 2026 07 03 |  |  |  | 3102-FZT-62004/3000-S-MC-B04 |  | NH-DJYYP3 1x2x1.5 | 441 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B04 | Одиночный |  | 3102-FZT-62004/3000-S-MC-B04 | 3000-S-SC-B01 | 3000-S-MC-B04 |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 8 | [12 empty] | Запись в БД произведена
287 | 3102 | Сombined Title | 3102-TZIA-62003 | SAI1000-01R | 3102-TZIA-62003 |  | 3102-Z-6201 | 3102-TZT-62003 | Т на выходе трубного пучка 3102-E-6201 | 3102-E-6201's tube-side outlet temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 150 | ℃ | -50 | 150 | ℃ |  |  | 90 | 95 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C182/3000-S-MC-B03 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C182 |  |  | 3102-TZT-62003/3102-S-JB-C182 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 0 | [12 empty] | Запись в БД произведена
289 | 3102 | Сombined Title | 3102-XZV-62001 | SKLPD0021-00 | 3102-XZV-62001 |  |  | 3102-XZV-62001 | Вход 3102-MX-6201, блок. отсечки | 3102-MX-6201 inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
290 | 3102 | Сombined Title | 3102-XZV-62001 | SKLPD0021-00 | 3102-XZV-62001 |  | 3102-Z-6201, 3102-Z-6291 | 3102-XZY-62001 | Вход 3102-MX-6201, блок. отсечки | 3102-MX-6201 inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR02 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3102-XZY-62001/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 1 | [12 empty] | Запись в БД произведена
291 | 3102 | Сombined Title | 3102-XZV-62001 | SKLPD0021-00 | 3102-XZV-62001 |  |  | 3102-XZZSC-62001 | Вход 3102-MX-6201, блок. отсечки (закрыт) | 3102-MX-6201 inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSC-62001/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 8 | [12 empty] | Запись в БД произведена
292 | 3102 | Сombined Title | 3102-XZV-62001 | SKLPD0021-00 | 3102-XZV-62001 |  |  | 3102-XZZSO-62001 | Вход 3102-MX-6201, блок. отсечки (открыт) | 3102-MX-6201 inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSO-62001/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 14 | [12 empty] | Запись в БД произведена
294 | 3102 | Сombined Title | 3102-XZV-62002 | SKLPD0021-00 | 3102-XZV-62002 |  |  | 3102-XZV-62002 | EB к 3102-MX-6201, блок. отсечки | EB to 3102-MX-6201 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
295 | 3102 | Сombined Title | 3102-XZV-62002 | SKLPD0021-00 | 3102-XZV-62002 |  | 3102-Z-6203, 3102-Z-6204, 3102-Z-6291 | 3102-XZY-62002 | EB к 3102-MX-6201, блок. отсечки | EB to 3102-MX-6201 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR03 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3102-XZY-62002/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 2 | [12 empty] | Запись в БД произведена
296 | 3102 | Сombined Title | 3102-XZV-62002 | SKLPD0021-00 | 3102-XZV-62002 |  |  | 3102-XZZSC-62002 | EB к 3102-MX-6201, блок. отсечки (закрыт) | EB to 3102-MX-6201 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSC-62002/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 9 | [12 empty] | Запись в БД произведена
297 | 3102 | Сombined Title | 3102-XZV-62002 | SKLPD0021-00 | 3102-XZV-62002 |  |  | 3102-XZZSO-62002 | EB к 3102-MX-6201, блок. отсечки (открыт) | EB to 3102-MX-6201 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSO-62002/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 15 | [12 empty] | Запись в БД произведена
299 | 3102 | Сombined Title | 3101-XZV-62003 | SKLPD0021-00 | 3101-XZV-62003 |  |  | 3101-XZV-62003 | Инициатор к 3102-MX-6202, блок. отсечки | initator to 3102-MX-6202 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
300 | 3102 | Сombined Title | 3101-XZV-62003 | SKLPD0021-00 | 3101-XZV-62003 |  | 3102-Z-6201, 3102-Z-6291 | 3101-XZY-62003 | Инициатор к 3102-MX-6202, блок. отсечки | initator to 3102-MX-6202 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D195/3000-S-MC-B11 | PR01 | NH-KYJYP3 16x2.5 | 426 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D195 |  |  | 3101-XZY-62003/3102-S-JB-D195 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 4 | [12 empty] | Запись в БД произведена
301 | 3102 | Сombined Title | 3101-XZV-62003 | SKLPD0021-00 | 3101-XZV-62003 |  |  | 3101-XZZSC-62003 | Инициатор к 3102-MX-6202, блок. отсечки (закрыт) | initator to 3102-MX-6202 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3101-XZZSC-62003/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 8 | [12 empty] | Запись в БД произведена
302 | 3102 | Сombined Title | 3101-XZV-62003 | SKLPD0021-00 | 3101-XZV-62003 |  |  | 3101-XZZSO-62003 | Инициатор к 3102-MX-6202, блок. отсечки (открыт) | initator to 3102-MX-6202 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3101-XZZSO-62003/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 31 | [12 empty] | Запись в БД произведена
304 | 3102 | Сombined Title | 3109-XZV-62022 | SKLPD0021-00 | 3109-XZV-62022 |  |  | 3109-XZV-62022 | Отс. клап. цирк. р-ра к 3102-MX-6201 | Circulating solution to 3102-MX-6201 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
305 | 3102 | Сombined Title | 3109-XZV-62022 | SKLPD0021-00 | 3109-XZV-62022 |  | 3102-Z-6201 | 3109-XZY-62022 | Отс. клап. цирк. р-ра к 3102-MX-6201 | Circulating solution to 3102-MX-6201 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR06 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3109-XZY-62022/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 9 | [12 empty] | Запись в БД произведена
306 | 3102 | Сombined Title | 3109-XZV-62022 | SKLPD0021-00 | 3109-XZV-62022 |  |  | 3109-XZZSC-62022 | Отс. клап. цирк. р-ра к 3102-MX-6201 (закрыт) | Circulating solution to 3102-MX-6201 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C174/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 450 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C174 |  |  | 3109-XZZSC-62022/3102-S-JB-C174 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 21 | [12 empty] | Запись в БД произведена
307 | 3102 | Сombined Title | 3109-XZV-62022 | SKLPD0021-00 | 3109-XZV-62022 |  |  | 3109-XZZSO-62022 | Отс. клап. цирк. р-ра к 3102-MX-6201 (открыт) | Circulating solution to 3102-MX-6201 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C174/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 450 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C174 |  |  | 3109-XZZSO-62022/3102-S-JB-C174 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 22 | [12 empty] | Запись в БД произведена
309 | 3102 | Сombined Title | 3101-XZV-62023 | SKLPD0021-00 | 3101-XZV-62023 |  |  | 3101-XZV-62023 | Отс. клап. стирола от 3101-F-6101A/B к 3102-MX-6201 | 3101-F-6101A/B's styrene to 3102-MX-6201 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
310 | 3102 | Сombined Title | 3101-XZV-62023 | SKLPD0021-00 | 3101-XZV-62023 |  | 3102-Z-6201, 3102-Z-6291 | 3101-XZY-62023 | Отс. клап. стирола от 3101-F-6101A/B к 3102-MX-6201 | 3101-F-6101A/B's styrene to 3102-MX-6201 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR01 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3101-XZY-62023/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 0 | [12 empty] | Запись в БД произведена
311 | 3102 | Сombined Title | 3101-XZV-62023 | SKLPD0021-00 | 3101-XZV-62023 |  |  | 3101-XZZSC-62023 | Отс. клап. стирола от F-6101A/B к MX-6201 (закрыт) | 3101-F-6101A/B's styrene to 3102-MX-6201 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C174/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 450 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C174 |  |  | 3101-XZZSC-62023/3102-S-JB-C174 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 17 | [12 empty] | Запись в БД произведена
312 | 3102 | Сombined Title | 3101-XZV-62023 | SKLPD0021-00 | 3101-XZV-62023 |  |  | 3101-XZZSO-62023 | Отс. клап. стирола от F-6101A/B к MX-6201 (открыт) | 3101-F-6101A/B's styrene to 3102-MX-6201 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C174/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 450 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C174 |  |  | 3101-XZZSO-62023/3102-S-JB-C174 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 18 | [12 empty] | Запись в БД произведена
314 | 3102 | Сombined Title | 3102-PZIA-62005A | SAI1000-01R | 3102-PZIA-62005A |  | 3102-Z-6204 | 3102-PZT-62005A | Р на выходе 3102-EJ-6202 | 3102-EJ-6202 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C179/3000-S-MC-B02 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C179 |  |  | 3102-PZT-62005A/3102-S-JB-C179 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 0 | [12 empty] | Запись в БД произведена
315 | 3102 | Сombined Title | 3102-PZIA-62005B | SAI1000-01R | 3102-PZIA-62005B |  | 3102-Z-6204 | 3102-PZT-62005B | Р на выходе 3102-EJ-6202 | 3102-EJ-6202 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C181/3000-S-MC-B02 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C181 |  |  | 3102-PZT-62005B/3102-S-JB-C181 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 0 | [12 empty] | Запись в БД произведена
316 | 3102 | Сombined Title | 3102-PZIA-62005C | SAI1000-01R | 3102-PZIA-62005C |  | 3102-Z-6204 | 3102-PZT-62005C | Р на выходе 3102-EJ-6202 | 3102-EJ-6202 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C182/3000-S-MC-B03 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C182 |  |  | 3102-PZT-62005C/3102-S-JB-C182 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 1 | [12 empty] | Запись в БД произведена
318 | 3102 | Сombined Title | 3102-TZIA-62005A | SAI1000-01R | 3102-TZIA-62005A |  | 3102-Z-6202, 3102-Z-6203 | 3102-TZT-62005A | Т 3102-R-6201 | 3102-R-6201 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-TZT-62005A/3102-S-JB-C138 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 1 | [12 empty] | Запись в БД произведена
319 | 3102 | Сombined Title | 3102-TZIA-62005B | SAI1000-01R | 3102-TZIA-62005B |  | 3102-Z-6202, 3102-Z-6203 | 3102-TZT-62005B | Т 3102-R-6201 | 3102-R-6201 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-TZT-62005B/3102-S-JB-C139 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 1 | [12 empty] | Запись в БД произведена
320 | 3102 | Сombined Title | 3102-TZIA-62005C | SAI1000-01R | 3102-TZIA-62005C |  | 3102-Z-6202, 3102-Z-6203 | 3102-TZT-62005C | Т 3102-R-6201 | 3102-R-6201 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C148/3000-S-MC-B03 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C148 |  |  | 3102-TZT-62005C/3102-S-JB-C148 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 8 | [12 empty] | Запись в БД произведена
322 | 3102 | Сombined Title | 3102-LZSA-62031A | SDI0010-01R | 3102-LZSA-62031A |  | 3102-Z-6222 | 3102-LZS-62031A | Ур. на входе 3102-P-6202A | 3102-P-6202A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3102-LZS-62031A/3102-S-JB-C142 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 5 | [12 empty] | Запись в БД произведена
324 | 3102 | Сombined Title | 3102-LZSA-62031B | SDI0010-01R | 3102-LZSA-62031B |  | 3102-Z-6222 | 3102-LZS-62031B | Ур. на входе 3102-P-6202B | 3102-P-6202B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3102-LZS-62031B/3102-S-JB-C143 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 7 | [12 empty] | Запись в БД произведена
326 | 3102 | Сombined Title | 3102-XZV-62004 | SKLPD0021-00 | 3102-XZV-62004 |  |  | 3102-XZV-62004 | Промывка EB | EB rinse | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
327 | 3102 | Сombined Title | 3102-XZV-62004 | SKLPD0021-00 | 3102-XZV-62004 |  | 3102-Z-6204 | 3102-XZY-62004 | Промывка EB | EB rinse | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D183/3000-S-MC-B11 | PR01 | NH-KYJYP3 16x2.5 | 434 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D183 |  |  | 3102-XZY-62004/3102-S-JB-D183 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 0 | [12 empty] | Запись в БД произведена
328 | 3102 | Сombined Title | 3102-XZV-62004 | SKLPD0021-00 | 3102-XZV-62004 |  |  | 3102-XZZSC-62004 | Промывка EB (закрыт) | EB rinse | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3102-XZZSC-62004/3102-S-JB-C180 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 23 | [12 empty] | Запись в БД произведена
329 | 3102 | Сombined Title | 3102-XZV-62004 | SKLPD0021-00 | 3102-XZV-62004 |  |  | 3102-XZZSO-62004 | Промывка EB (открыт) | EB rinse | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3102-XZZSO-62004/3102-S-JB-C180 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 27 | [12 empty] | Запись в БД произведена
331 | 3102 | Сombined Title | 3102-XZV-62006 | SKLPD0021-00 | 3102-XZV-62006 |  |  | 3102-XZV-62006 | Азот к отх. газу, блок. отсечки | Nitrogen to off gas Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
332 | 3102 | Сombined Title | 3102-XZV-62006 | SKLPD0021-00 | 3102-XZV-62006 |  | 3102-Z-6204 | 3102-XZY-62006 | Азот к отх. газу, блок. отсечки | Nitrogen to off gas Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D195/3000-S-MC-B11 | PR02 | NH-KYJYP3 16x2.5 | 426 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D195 |  |  | 3102-XZY-62006/3102-S-JB-D195 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 5 | [12 empty] | Запись в БД произведена
333 | 3102 | Сombined Title | 3102-XZV-62006 | SKLPD0021-00 | 3102-XZV-62006 |  |  | 3102-XZZSC-62006 | Азот к отх. газу, блок. отсечки (закрыт) | Nitrogen to off gas Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3102-XZZSC-62006/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 0 | [12 empty] | Запись в БД произведена
334 | 3102 | Сombined Title | 3102-XZV-62006 | SKLPD0021-00 | 3102-XZV-62006 |  |  | 3102-XZZSO-62006 | Азот к отх. газу, блок. отсечки (открыт) | Nitrogen to off gas Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3102-XZZSO-62006/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 4 | [12 empty] | Запись в БД произведена
336 | 3102 | Сombined Title | 3102-XZV-62007 | SKLPD0021-00 | 3102-XZV-62007 |  |  | 3102-XZV-62007 | Выход 3102-EJ-6201, блок. отсечки | 3102-EJ-6201 outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
337 | 3102 | Сombined Title | 3102-XZV-62007 | SKLPD0021-00 | 3102-XZV-62007 |  | 3102-Z-6204, 3102-Z-6291 | 3102-XZY-62007 | Выход 3102-EJ-6201, блок. отсечки | 3102-EJ-6201 outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D195/3000-S-MC-B11 | PR03 | NH-KYJYP3 16x2.5 | 426 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D195 |  |  | 3102-XZY-62007/3102-S-JB-D195 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 6 | [12 empty] | Запись в БД произведена
338 | 3102 | Сombined Title | 3102-XZV-62007 | SKLPD0021-00 | 3102-XZV-62007 |  |  | 3102-XZZSC-62007 | Выход 3102-EJ-6201, блок. отсечки (закрыт) | 3102-EJ-6201 outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3102-XZZSC-62007/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 1 | [12 empty] | Запись в БД произведена
339 | 3102 | Сombined Title | 3102-XZV-62007 | SKLPD0021-00 | 3102-XZV-62007 |  |  | 3102-XZZSO-62007 | Выход 3102-EJ-6201, блок. отсечки (открыт) | 3102-EJ-6201 outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3102-XZZSO-62007/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 5 | [12 empty] | Запись в БД произведена
341 | 3102 | Сombined Title | 3102-XZV-62101 | SKLPD0021-00 | 3102-XZV-62101 |  |  | 3102-XZV-62101 | Вход 3102-P-6202AB | 3102-P-6202AB Inlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
342 | 3102 | Сombined Title | 3102-XZV-62101 | SKLPD0021-00 | 3102-XZV-62101 |  | 3102-Z-6247 | 3102-XZY-62101 | Вход 3102-P-6202AB | 3102-P-6202AB Inlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR10 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3102-XZY-62101/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 6 | [12 empty] | Запись в БД произведена
343 | 3102 | Сombined Title | 3102-XZV-62101 | SKLPD0021-00 | 3102-XZV-62101 |  |  | 3102-XZZSC-62101 | Вход 3102-P-6202AB (закрыт) | 3102-P-6202AB Inlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSC-62101/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 12 | [12 empty] | Запись в БД произведена
345 | 3102 | Сombined Title | 3102-XZV-62102 | SKLPD0021-00 | 3102-XZV-62102 |  |  | 3102-XZV-62102 | Выход 3102-P-6202AB | 3102-P-6202AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
346 | 3102 | Сombined Title | 3102-XZV-62102 | SKLPD0021-00 | 3102-XZV-62102 |  | 3102-Z-6247 | 3102-XZY-62102 | Выход 3102-P-6202AB | 3102-P-6202AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D158/3000-S-MC-B12 | PR02 | NH-KYJYP3 16x2.5 | 473 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D158 |  |  | 3102-XZY-62102/3102-S-JB-D158 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 26 | [12 empty] | Запись в БД произведена
347 | 3102 | Сombined Title | 3102-XZV-62102 | SKLPD0021-00 | 3102-XZV-62102 |  |  | 3102-XZZSC-62102 | Выход 3102-P-6202AB (закрыт) | 3102-P-6202AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C156/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 8x2x1.0 | 446 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C156 |  |  | 3102-XZZSC-62102/3102-S-JB-C156 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 13 | [12 empty] | Запись в БД произведена
349 | 3102 | Сombined Title | 3102-XZV-62021 | SKLPD0021-00 | 3102-XZV-62021 |  |  | 3102-XZV-62021 | Масл. дренаж к 3103-V-6208, блок. отсечки | Oily drain to 3103-V-6208 interlock to cut offf | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
350 | 3102 | Сombined Title | 3102-XZV-62021 | SKLPD0021-00 | 3102-XZV-62021 |  | 3102-Z-6291 | 3102-XZY-62021 | Масл. дренаж к 3103-V-6208, блок. отсечки | Oily drain to 3103-V-6208 interlock to cut offf | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR04 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3102-XZY-62021/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 3 | [12 empty] | Запись в БД произведена
351 | 3102 | Сombined Title | 3102-XZV-62021 | SKLPD0021-00 | 3102-XZV-62021 |  |  | 3102-XZZSC-62021 | Масл. дренаж к 3103-V-6208, блок. отсечки (закрыт) | Oily drain to 3103-V-6208 interlock to cut offf | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSC-62021/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 10 | [12 empty] | Запись в БД произведена
352 | 3102 | Сombined Title | 3102-XZV-62021 | SKLPD0021-00 | 3102-XZV-62021 |  |  | 3102-XZZSO-62021 | Масл. дренаж к 3103-V-6208, блок. отсечки (открыт) | Oily drain to 3103-V-6208 interlock to cut offf | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSO-62021/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 16 | [12 empty] | Запись в БД произведена
354 | 3102 | Сombined Title | 3102-XZV-62027 | SKLPD0021-00 | 3102-XZV-62027 |  |  | 3102-XZV-62027 | Отс. клап. на выходе 3109-P-6703 | 3109-P-6703 outlet cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
355 | 3102 | Сombined Title | 3102-XZV-62027 | SKLPD0021-00 | 3102-XZV-62027 |  | 3102-Z-6204, 3102-Z-6291, 3102-Z-6203 | 3102-XZY-62027 | Отс. клап. на выходе 3109-P-6703 | 3109-P-6703 outlet cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR09 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3102-XZY-62027/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 4 | [12 empty] | Запись в БД произведена
356 | 3102 | Сombined Title | 3102-XZV-62027 | SKLPD0021-00 | 3102-XZV-62027 |  |  | 3102-XZZSC-62027 | Отс. клап. на выходе 3109-P-6703 (закрыт) | 3109-P-6703 outlet cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSC-62027/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 11 | [12 empty] | Запись в БД произведена
357 | 3102 | Сombined Title | 3102-XZV-62027 | SKLPD0021-00 | 3102-XZV-62027 |  |  | 3102-XZZSO-62027 | Отс. клап. на выходе 3109-P-6703 (открыт) | 3109-P-6703 outlet cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSO-62027/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 17 | [12 empty] | Запись в БД произведена
359 | 3102 | Сombined Title | 3102-XZV-62028 | SKLPD0021-00 | 3102-XZV-62028 |  |  | 3102-XZV-62028 | Отс. клап. EB на входе 3102-R-6202 | 3102-R-6202's EB inlet cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
360 | 3102 | Сombined Title | 3102-XZV-62028 | SKLPD0021-00 | 3102-XZV-62028 |  | 3102-Z-6209, 3102-Z-6291, 3102-Z-6208 | 3102-XZY-62028 | Отс. клап. EB на входе 3102-R-6202 | 3102-R-6202's EB inlet cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D183/3000-S-MC-B11 | PR04 | NH-KYJYP3 16x2.5 | 434 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D183 |  |  | 3102-XZY-62028/3102-S-JB-D183 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 3 | [12 empty] | Запись в БД произведена
361 | 3102 | Сombined Title | 3102-XZV-62028 | SKLPD0021-00 | 3102-XZV-62028 |  |  | 3102-XZZSC-62028 | Отс. клап. EB на входе 3102-R-6202 (закрыт) | 3102-R-6202's EB inlet cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3102-XZZSC-62028/3102-S-JB-C180 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 26 | [12 empty] | Запись в БД произведена
362 | 3102 | Сombined Title | 3102-XZV-62028 | SKLPD0021-00 | 3102-XZV-62028 |  |  | 3102-XZZSO-62028 | Отс. клап. EB на входе 3102-R-6202 (открыт) | 3102-R-6202's EB inlet cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3102-XZZSO-62028/3102-S-JB-C180 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 30 | [12 empty] | Запись в БД произведена
364 | 3102 | Сombined Title | 3102-TZIA-66351A | SAI1000-01R | 3102-TZIA-66351A |  | 3102-Z-6247 | 3102-TZT-66351A | Т подшипника 3102-P-6202A | 3102-P-6202A Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-TZT-66351A/3102-S-JB-C138 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 0 | [12 empty] | Запись в БД произведена
365 | 2202 | Сombined Title | 3102-MXI-06202A | SDO0001-01 | 3102-MXI-06202A |  | 3102-Z-6222, 3102-Z-6247, 3102-Z-6290 | 3102-MXI-06202A | SIS стоп насоса рецикла первого преполим. 3102-P-6202A | First Pre-Polymerizer Reflux Pump 3102-P-6202A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6202 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 3 | [12 empty] | Запись в БД произведена
367 | 3102 | Сombined Title | 3102-TZIA-66351B | SAI1000-01R | 3102-TZIA-66351B |  | 3102-Z-6247 | 3102-TZT-66351B | Т подшипника 3102-P-6202B | 3102-P-6202B Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-TZT-66351B/3102-S-JB-C139 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 0 | [12 empty] | Запись в БД произведена
368 | 2202 | Сombined Title | 3102-MXI-16202A | SDO0001-01 | 3102-MXI-16202A |  | 3102-Z-6222, 3102-Z-6247, 3102-Z-6290 | 3102-MXI-16202A | SIS стоп насоса рецикла первого преполим. 3102-P-6202B | First Pre-Polymerizer Reflux Pump 3102-P-6202B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6202 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 10 | [12 empty] | Запись в БД произведена
370 | 3102 | Сombined Title | 3102-PZIA-62007A | SAI1000-01R | 3102-PZIA-62007A |  | 3102-Z-6205 | 3102-PZT-62007A | Р нагнетания 3102-P-6201B | 3102-P-6201B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-PZT-62007A/3102-S-JB-C138 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 2 | [12 empty] | Запись в БД произведена
371 | 3102 | Сombined Title | 3102-PZIA-62007B | SAI1000-01R | 3102-PZIA-62007B |  | 3102-Z-6205 | 3102-PZT-62007B | Р нагнетания 3102-P-6201B | 3102-P-6201B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-PZT-62007B/3102-S-JB-C139 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 2 | [12 empty] | Запись в БД произведена
372 | 3102 | Сombined Title | 3102-PZIA-62007C | SAI1000-01R | 3102-PZIA-62007C |  | 3102-Z-6205 | 3102-PZT-62007C | Р нагнетания 3102-P-6201B | 3102-P-6201B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C148/3000-S-MC-B03 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C148 |  |  | 3102-PZT-62007C/3102-S-JB-C148 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 9 | [12 empty] | Запись в БД произведена
374 | 3102 | Сombined Title | 3102-PZIA-62008A | SAI1000-01R | 3102-PZIA-62008A |  | 3102-Z-6206 | 3102-PZT-62008A | Р нагнетания 3102-P-6201A | 3102-P-6201A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-PZT-62008A/3102-S-JB-C138 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 3 | [12 empty] | Запись в БД произведена
375 | 3102 | Сombined Title | 3102-PZIA-62008B | SAI1000-01R | 3102-PZIA-62008B |  | 3102-Z-6206 | 3102-PZT-62008B | Р нагнетания 3102-P-6201A | 3102-P-6201A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-PZT-62008B/3102-S-JB-C139 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 3 | [12 empty] | Запись в БД произведена
376 | 3102 | Сombined Title | 3102-PZIA-62008C | SAI1000-01R | 3102-PZIA-62008C |  | 3102-Z-6206 | 3102-PZT-62008C | Р нагнетания 3102-P-6201A | 3102-P-6201A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C148/3000-S-MC-B03 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C148 |  |  | 3102-PZT-62008C/3102-S-JB-C148 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 10 | [12 empty] | Запись в БД произведена
378 | 2202 | 3102 | 3102-MXI-76201A | SDO0001-01 | 3102-MXI-76201A |  | 3102-Z-6290 | 3102-MXI-76201A | SIS стоп мешалки первого преполим. 3102-AG-6201 | First Pre-Polymerizer Agitator 3102-AG-6201 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6203 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 16 | [12 empty] | Запись в БД произведена
380 | 2202 | Сombined Title | 3102-MXI-06201A | SDO0001-01 | 3102-MXI-06201A |  | 3102-Z-6205, 3102-Z-6290 | 3102-MXI-06201A | SIS стоп расплавного насоса первого преполим. 3102-P-6201A | First Pre-Polymerizer Melt Pump 3102-P-6201A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6203 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 2 | [12 empty] | Запись в БД произведена
381 | 2202 | Сombined Title | 3102-MII-06201 | SAI1000-01R | 3102-MII-06201 |  | 3102-Z-6205 | 3102-MII-06201 | Ток расплавного насоса первого преполим. 3102-P-6201A | First Pre-Polymerizer Melt Pump 3102-P-6201A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6203 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 0 | [12 empty] | Запись в БД произведена
383 | 2202 | Сombined Title | 3102-MXI-16201A | SDO0001-01 | 3102-MXI-16201A |  | 3102-Z-6206, 3102-Z-6290 | 3102-MXI-16201A | SIS стоп расплавного насоса первого преполим. 3102-P-6201B | First Pre-Polymerizer Melt Pump 3102-P-6201B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6203 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 9 | [12 empty] | Запись в БД произведена
384 | 2202 | Сombined Title | 3102-MII-16201 | SAI1000-01R | 3102-MII-16201 |  | 3102-Z-6206 | 3102-MII-16201 | Ток расплавного насоса первого преполим. 3102-P-6201B | First Pre-Polymerizer Melt Pump 3102-P-6201B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6203 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 1 | [12 empty] | Запись в БД произведена
386 | 3102 | Сombined Title | 3102-PZIA-62009A | SAI1000-01R | 3102-PZIA-62009A |  | 3102-Z-6209 | 3102-PZT-62009A | Р на выходе 3102-EJ-6204 | 3102-EJ-6204 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C179/3000-S-MC-B02 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C179 |  |  | 3102-PZT-62009A/3102-S-JB-C179 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 1 | [12 empty] | Запись в БД произведена
387 | 3102 | Сombined Title | 3102-PZIA-62009B | SAI1000-01R | 3102-PZIA-62009B |  | 3102-Z-6209 | 3102-PZT-62009B | Р на выходе 3102-EJ-6204 | 3102-EJ-6204 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C181/3000-S-MC-B02 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C181 |  |  | 3102-PZT-62009B/3102-S-JB-C181 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 1 | [12 empty] | Запись в БД произведена
388 | 3102 | Сombined Title | 3102-PZIA-62009C | SAI1000-01R | 3102-PZIA-62009C |  | 3102-Z-6209 | 3102-PZT-62009C | Р на выходе 3102-EJ-6204 | 3102-EJ-6204 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C182/3000-S-MC-B03 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C182 |  |  | 3102-PZT-62009C/3102-S-JB-C182 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 2 | [12 empty] | Запись в БД произведена
390 | 3102 | Сombined Title | 3102-TZIA-62011A | SAI1000-01R | 3102-TZIA-62011A |  | 3102-Z-6207, 3102-Z-6208 | 3102-TZT-62011A | Т 3102-R-6202 | 3102-R-6202 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-TZT-62011A/3102-S-JB-C138 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 4 | [12 empty] | Запись в БД произведена
391 | 3102 | Сombined Title | 3102-TZIA-62011B | SAI1000-01R | 3102-TZIA-62011B |  | 3102-Z-6207, 3102-Z-6208 | 3102-TZT-62011B | Т 3102-R-6202 | 3102-R-6202 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-TZT-62011B/3102-S-JB-C139 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 4 | [12 empty] | Запись в БД произведена
392 | 3102 | Сombined Title | 3102-TZIA-62011C | SAI1000-01R | 3102-TZIA-62011C |  | 3102-Z-6207, 3102-Z-6208 | 3102-TZT-62011C | Т 3102-R-6202 | 3102-R-6202 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C148/3000-S-MC-B03 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C148 |  |  | 3102-TZT-62011C/3102-S-JB-C148 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 11 | [12 empty] | Запись в БД произведена
394 | 3102 | Сombined Title | 3102-LZSA-62032A | SDI0010-01R | 3102-LZSA-62032A |  | 3102-Z-6223 | 3102-LZS-62032A | Ур. на входе 3102-P-6204A | 3102-P-6204A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C128/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 454 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C128 |  |  | 3102-LZS-62032A/3102-S-JB-C128 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 22 | [12 empty] | Запись в БД произведена
396 | 3102 | Сombined Title | 3102-LZSA-62032B | SDI0010-01R | 3102-LZSA-62032B |  | 3102-Z-6223 | 3102-LZS-62032B | Ур. на входе 3102-P-6204B | 3102-P-6204B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C129/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 448 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C129 |  |  | 3102-LZS-62032B/3102-S-JB-C129 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 23 | [12 empty] | Запись в БД произведена
398 | 3102 | Сombined Title | 3102-XZV-62008 | SKLPD0021-00 | 3102-XZV-62008 |  |  | 3102-XZV-62008 | 3102-P-6201A/B к 3102-R-6202, блок. отсечки | 3102-P-6201A/B to 3102-R-6202 interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
399 | 3102 | Сombined Title | 3102-XZV-62008 | SKLPD0021-00 | 3102-XZV-62008 |  | 3102-Z-6204, 3102-Z-6209 | 3102-XZY-62008 | 3102-P-6201A/B к 3102-R-6202, блок. отсечки | 3102-P-6201A/B to 3102-R-6202 interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR01 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3102-XZY-62008/3102-S-JB-D144 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 0 | [12 empty] | Запись в БД произведена
400 | 3102 | Сombined Title | 3102-XZV-62008 | SKLPD0021-00 | 3102-XZV-62008 |  |  | 3102-XZZSC-62008 | 3102-P-6201A/B к 3102-R-6202, блок. отсечки (закрыт) | 3102-P-6201A/B to 3102-R-6202 interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3102-XZZSC-62008/3102-S-JB-C141 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 0 | [12 empty] | Запись в БД произведена
401 | 3102 | Сombined Title | 3102-XZV-62008 | SKLPD0021-00 | 3102-XZV-62008 |  |  | 3102-XZZSO-62008 | 3102-P-6201A/B к 3102-R-6202, блок. отсечки (открыт) | 3102-P-6201A/B to 3102-R-6202 interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3102-XZZSO-62008/3102-S-JB-C141 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 3 | [12 empty] | Запись в БД произведена
403 | 3102 | Сombined Title | 3102-XZV-62009 | SKLPD0021-00 | 3102-XZV-62009 |  |  | 3102-XZV-62009 | Промывка EB | EB rinse | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
404 | 3102 | Сombined Title | 3102-XZV-62009 | SKLPD0021-00 | 3102-XZV-62009 |  | 3102-Z-6209 | 3102-XZY-62009 | Промывка EB | EB rinse | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D183/3000-S-MC-B11 | PR02 | NH-KYJYP3 16x2.5 | 434 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D183 |  |  | 3102-XZY-62009/3102-S-JB-D183 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 1 | [12 empty] | Запись в БД произведена
405 | 3102 | Сombined Title | 3102-XZV-62009 | SKLPD0021-00 | 3102-XZV-62009 |  |  | 3102-XZZSC-62009 | Промывка EB (закрыт) | EB rinse | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3102-XZZSC-62009/3102-S-JB-C180 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 24 | [12 empty] | Запись в БД произведена
406 | 3102 | Сombined Title | 3102-XZV-62009 | SKLPD0021-00 | 3102-XZV-62009 |  |  | 3102-XZZSO-62009 | Промывка EB (открыт) | EB rinse | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3102-XZZSO-62009/3102-S-JB-C180 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 28 | [12 empty] | Запись в БД произведена
408 | 3102 | Сombined Title | 3102-XZV-62010 | SKLPD0021-00 | 3102-XZV-62010 |  |  | 3102-XZV-62010 | EB к 3102-R-6202, блок. отсечки | EB to 3102-R-6202 interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
409 | 3102 | Сombined Title | 3102-XZV-62010 | SKLPD0021-00 | 3102-XZV-62010 |  | 3102-Z-6208, 3102-Z-6209, 3102-Z-6291 | 3102-XZY-62010 | EB к 3102-R-6202, блок. отсечки | EB to 3102-R-6202 interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D183/3000-S-MC-B11 | PR03 | NH-KYJYP3 16x2.5 | 434 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D183 |  |  | 3102-XZY-62010/3102-S-JB-D183 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 2 | [12 empty] | Запись в БД произведена
410 | 3102 | Сombined Title | 3102-XZV-62010 | SKLPD0021-00 | 3102-XZV-62010 |  |  | 3102-XZZSC-62010 | EB к 3102-R-6202, блок. отсечки (закрыт) | EB to 3102-R-6202 interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3102-XZZSC-62010/3102-S-JB-C180 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 25 | [12 empty] | Запись в БД произведена
411 | 3102 | Сombined Title | 3102-XZV-62010 | SKLPD0021-00 | 3102-XZV-62010 |  |  | 3102-XZZSO-62010 | EB к 3102-R-6202, блок. отсечки (открыт) | EB to 3102-R-6202 interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C180/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C180 |  |  | 3102-XZZSO-62010/3102-S-JB-C180 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 29 | [12 empty] | Запись в БД произведена
413 | 3102 | Сombined Title | 3102-XZV-62011 | SKLPD0021-00 | 3102-XZV-62011 |  |  | 3102-XZV-62011 | Азот к отх. газу, блок. отсечки | Nitrogen to off gas interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
414 | 3102 | Сombined Title | 3102-XZV-62011 | SKLPD0021-00 | 3102-XZV-62011 |  | 3102-Z-6209 | 3102-XZY-62011 | Азот к отх. газу, блок. отсечки | Nitrogen to off gas interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D195/3000-S-MC-B11 | PR04 | NH-KYJYP3 16x2.5 | 426 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D195 |  |  | 3102-XZY-62011/3102-S-JB-D195 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 7 | [12 empty] | Запись в БД произведена
415 | 3102 | Сombined Title | 3102-XZV-62011 | SKLPD0021-00 | 3102-XZV-62011 |  |  | 3102-XZZSC-62011 | Азот к отх. газу, блок. отсечки (закрыт) | Nitrogen to off gas interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3102-XZZSC-62011/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 2 | [12 empty] | Запись в БД произведена
416 | 3102 | Сombined Title | 3102-XZV-62011 | SKLPD0021-00 | 3102-XZV-62011 |  |  | 3102-XZZSO-62011 | Азот к отх. газу, блок. отсечки (открыт) | Nitrogen to off gas interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3102-XZZSO-62011/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 6 | [12 empty] | Запись в БД произведена
418 | 3102 | Сombined Title | 3102-XZV-62012 | SKLPD0021-00 | 3102-XZV-62012 |  |  | 3102-XZV-62012 | Выход 3102-EJ-6203, блок. отсечки | 3102-EJ-6203 outlet interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
419 | 3102 | Сombined Title | 3102-XZV-62012 | SKLPD0021-00 | 3102-XZV-62012 |  | 3102-Z-6209, 3102-Z-6291 | 3102-XZY-62012 | Выход 3102-EJ-6203, блок. отсечки | 3102-EJ-6203 outlet interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D195/3000-S-MC-B11 | PR05 | NH-KYJYP3 16x2.5 | 426 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D195 |  |  | 3102-XZY-62012/3102-S-JB-D195 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 8 | [12 empty] | Запись в БД произведена
420 | 3102 | Сombined Title | 3102-XZV-62012 | SKLPD0021-00 | 3102-XZV-62012 |  |  | 3102-XZZSC-62012 | Выход 3102-EJ-6203, блок. отсечки (закрыт) | 3102-EJ-6203 outlet interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3102-XZZSC-62012/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 3 | [12 empty] | Запись в БД произведена
421 | 3102 | Сombined Title | 3102-XZV-62012 | SKLPD0021-00 | 3102-XZV-62012 |  |  | 3102-XZZSO-62012 | Выход 3102-EJ-6203, блок. отсечки (открыт) | 3102-EJ-6203 outlet interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C192/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 422 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C192 |  |  | 3102-XZZSO-62012/3102-S-JB-C192 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 7 | [12 empty] | Запись в БД произведена
423 | 3102 | Сombined Title | 3102-XZV-62015 | SKLPD0021-00 | 3102-XZV-62015 |  |  | 3102-XZV-62015 | Поток 3102-MX-6205, отсечка подачи | 3102-MX-6205 stream cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
424 | 3102 | Сombined Title | 3102-XZV-62015 | SKLPD0021-00 | 3102-XZV-62015 |  | 3102-Z-6209, 3102-Z-6291 | 3102-XZY-62015 | Поток 3102-MX-6205, отсечка подачи | 3102-MX-6205 stream cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D158/3000-S-MC-B12 | PR01 | NH-KYJYP3 16x2.5 | 473 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D158 |  |  | 3102-XZY-62015/3102-S-JB-D158 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 25 | [12 empty] | Запись в БД произведена
425 | 3102 | Сombined Title | 3102-XZV-62015 | SKLPD0021-00 | 3102-XZV-62015 |  |  | 3102-XZZSC-62015 | Поток 3102-MX-6205, отсечка подачи (закрыт) | 3102-MX-6205 stream cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C156/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 446 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C156 |  |  | 3102-XZZSC-62015/3102-S-JB-C156 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 12 | [12 empty] | Запись в БД произведена
426 | 3102 | Сombined Title | 3102-XZV-62015 | SKLPD0021-00 | 3102-XZV-62015 |  |  | 3102-XZZSO-62015 | Поток 3102-MX-6205, отсечка подачи (открыт) | 3102-MX-6205 stream cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C156/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 446 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C156 |  |  | 3102-XZZSO-62015/3102-S-JB-C156 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 14 | [12 empty] | Запись в БД произведена
428 | 3102 | Сombined Title | 3102-XZV-62103 | SKLPD0021-00 | 3102-XZV-62103 |  |  | 3102-XZV-62103 | Вход 3102-P-6204AB | 3102-P-6204AB Inlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
429 | 3102 | Сombined Title | 3102-XZV-62103 | SKLPD0021-00 | 3102-XZV-62103 |  | 3102-Z-6248 | 3102-XZY-62103 | Вход 3102-P-6204AB | 3102-P-6204AB Inlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR11 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3102-XZY-62103/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 7 | [12 empty] | Запись в БД произведена
430 | 3102 | Сombined Title | 3102-XZV-62103 | SKLPD0021-00 | 3102-XZV-62103 |  |  | 3102-XZZSC-62103 | Вход 3102-P-6204AB (закрыт) | 3102-P-6204AB Inlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3102-XZZSC-62103/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 13 | [12 empty] | Запись в БД произведена
432 | 3102 | Сombined Title | 3102-XZV-62104 | SKLPD0021-00 | 3102-XZV-62104 |  |  | 3102-XZV-62104 | Выход 3102-P-6204AB | 3102-P-6204AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
433 | 3102 | Сombined Title | 3102-XZV-62104 | SKLPD0021-00 | 3102-XZV-62104 |  | 3102-Z-6248 | 3102-XZY-62104 | Выход 3102-P-6204AB | 3102-P-6204AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR13 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3102-XZY-62104/3102-S-JB-D145 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 6 | [12 empty] | Запись в БД произведена
434 | 3102 | Сombined Title | 3102-XZV-62104 | SKLPD0021-00 | 3102-XZV-62104 |  |  | 3102-XZZSC-62104 | Выход 3102-P-6204AB (закрыт) | 3102-P-6204AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR13 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3102-XZZSC-62104/3102-S-JB-C141 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 2 | [12 empty] | Запись в БД произведена
436 | 3102 | Сombined Title | 3102-TZIA-66353A | SAI1000-01R | 3102-TZIA-66353A |  | 3102-Z-6248 | 3102-TZT-66353A | Т подшипника 3102-P-6204A | 3102-P-6204A Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-TZT-66353A/3000-S-MC-B02 |  | NH-IA-DJYYP3 1x2x1.5 | 536 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B02 | Одиночный |  | 3102-TZT-66353A/3000-S-MC-B02 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 11 | [12 empty] | Запись в БД произведена
437 | 2202 | Сombined Title | 3102-MXI-06204A | SDO0001-01 | 3102-MXI-06204A |  | 3102-Z-6223, 3102-Z-6248, 3102-Z-6290 | 3102-MXI-06204A | SIS стоп насоса рецикла второго преполим. 3102-P-6204A | Second Pre-Polymerizer Reflux Pump 3102-P-6204A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6204 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 5 | [12 empty] | Запись в БД произведена
439 | 3102 | Сombined Title | 3102-TZIA-66353B | SAI1000-01R | 3102-TZIA-66353B |  | 3102-Z-6248 | 3102-TZT-66353B | Т подшипника 3102-P-6204B | 3102-P-6204B Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3102-TZT-66353B/3000-S-MC-B02 |  | NH-IA-DJYYP3 1x2x1.5 | 536 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B02 | Одиночный |  | 3102-TZT-66353B/3000-S-MC-B02 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 12 | [12 empty] | Запись в БД произведена
440 | 2202 | Сombined Title | 3102-MXI-16204A | SDO0001-01 | 3102-MXI-16204A |  | 3102-Z-6223, 3102-Z-6248, 3102-Z-6290 | 3102-MXI-16204A | SIS стоп насоса рецикла второго преполим. 3102-P-6204B | Second Pre-Polymerizer Reflux Pump 3102-P-6204B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6204 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 12 | [12 empty] | Запись в БД произведена
442 | 3102 | Сombined Title | 3102-PZIA-62011A | SAI1000-01R | 3102-PZIA-62011A |  | 3102-Z-6210, 3102-Z-6211 | 3102-PZT-62011A | Р нагнетания 3102-P-6203A/B | 3102-P-6203A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,55 | 1,7 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-PZT-62011A/3102-S-JB-C138 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 5 | [12 empty] | Запись в БД произведена
443 | 3102 | Сombined Title | 3102-PZIA-62011B | SAI1000-01R | 3102-PZIA-62011B |  | 3102-Z-6210, 3102-Z-6211 | 3102-PZT-62011B | Р нагнетания 3102-P-6203A/B | 3102-P-6203A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,55 | 1,7 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-PZT-62011B/3102-S-JB-C139 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 5 | [12 empty] | Запись в БД произведена
444 | 3102 | Сombined Title | 3102-PZIA-62011C | SAI1000-01R | 3102-PZIA-62011C |  | 3102-Z-6210, 3102-Z-6211 | 3102-PZT-62011C | Р нагнетания 3102-P-6203A/B | 3102-P-6203A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,55 | 1,7 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C148/3000-S-MC-B03 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C148 |  |  | 3102-PZT-62011C/3102-S-JB-C148 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 12 | [12 empty] | Запись в БД произведена
446 | 3102 | Сombined Title | 3102-XZV-62013 | SKLPD0021-00 | 3102-XZV-62013 |  |  | 3102-XZV-62013 | Поток 3102-MX-6203, отсечка подачи | 3102-MX-6203's stream cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
447 | 3102 | Сombined Title | 3102-XZV-62013 | SKLPD0021-00 | 3102-XZV-62013 |  | 3102-Z-6209, 3102-Z-6291 | 3102-XZY-62013 | Поток 3102-MX-6203, отсечка подачи | 3102-MX-6203's stream cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D158/3000-S-MC-B12 | PR06 | NH-KYJYP3 16x2.5 | 473 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D158 |  |  | 3102-XZY-62013/3102-S-JB-D158 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 24 | [12 empty] | Запись в БД произведена
448 | 3102 | Сombined Title | 3102-XZV-62013 | SKLPD0021-00 | 3102-XZV-62013 |  |  | 3102-XZZSC-62013 | Поток 3102-MX-6203, отсечка подачи (закрыт) | 3102-MX-6203's stream cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3102-XZZSC-62013/3102-S-JB-C154 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 16 | [12 empty] | Запись в БД произведена
449 | 3102 | Сombined Title | 3102-XZV-62013 | SKLPD0021-00 | 3102-XZV-62013 |  |  | 3102-XZZSO-62013 | Поток 3102-MX-6203, отсечка подачи (открыт) | 3102-MX-6203's stream cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3102-XZZSO-62013/3102-S-JB-C154 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 17 | [12 empty] | Запись в БД произведена
451 | 3102 | Сombined Title | 3102-XZV-62014 | SKLPD0021-00 | 3102-XZV-62014 |  |  | 3102-XZV-62014 | 3102-P-6203A/B к 3102-MX-6203, блок. отсечки | 3102-P-6203A/B to 3102-MX-6203 interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
452 | 3102 | Сombined Title | 3102-XZV-62014 | SKLPD0021-00 | 3102-XZV-62014 |  | 3102-Z-6209, 3102-Z-6291 | 3102-XZY-62014 | 3102-P-6203A/B к 3102-MX-6203, блок. отсечки | 3102-P-6203A/B to 3102-MX-6203 interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR01 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3102-XZY-62014/3102-S-JB-D145 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 5 | [12 empty] | Запись в БД произведена
453 | 3102 | Сombined Title | 3102-XZV-62014 | SKLPD0021-00 | 3102-XZV-62014 |  |  | 3102-XZZSC-62014 | 3102-P-6203A/B к 3102-MX-6203, блок. отсечки (закрыт) | 3102-P-6203A/B to 3102-MX-6203 interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3102-XZZSC-62014/3102-S-JB-C141 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 1 | [12 empty] | Запись в БД произведена
454 | 3102 | Сombined Title | 3102-XZV-62014 | SKLPD0021-00 | 3102-XZV-62014 |  |  | 3102-XZZSO-62014 | 3102-P-6203A/B к 3102-MX-6203, блок. отсечки (открыт) | 3102-P-6203A/B to 3102-MX-6203 interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6205 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3102-XZZSO-62014/3102-S-JB-C141 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 4 | [12 empty] | Запись в БД произведена
456 | 2202 | 3102 | 3102-MXI-76202A | SDO0001-01 | 3102-MXI-76202A |  | 3102-Z-6290 | 3102-MXI-76202A | SIS стоп мешалки второго преполим. 3102-AG-6202 | Second Pre-Polymerizer Agitator 3102-AG-6202 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6205 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 17 | [12 empty] | Запись в БД произведена
458 | 2202 | Сombined Title | 3102-MXI-06203A | SDO0001-01 | 3102-MXI-06203A |  | 3102-Z-6210, 3102-Z-6290 | 3102-MXI-06203A | SIS стоп расплавного насоса второго преполим. 3102-P-6203A | Second Pre-Polymerizer Melt Pump 3102-P-6203A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6205 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 4 | [12 empty] | Запись в БД произведена
459 | 2202 | 3102 | 3102-MII-06203 | SAI1000-01R | 3102-MII-06203 |  | 3102-Z-6210 | 3102-MII-06203 | Ток расплавного насоса второго преполим. 3102-P-6203A | Second Pre-Polymerizer Melt Pump 3102-P-6203A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6205 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 2 | [12 empty] | Запись в БД произведена
461 | 2202 | Сombined Title | 3102-MXI-16203A | SDO0001-01 | 3102-MXI-16203A |  | 3102-Z-6211, 3102-Z-6290 | 3102-MXI-16203A | SIS стоп расплавного насоса второго преполим. 3102-P-6203B | Second Pre-Polymerizer Melt Pump 3102-P-6203B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6205 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 11 | [12 empty] | Запись в БД произведена
462 | 2202 | 3102 | 3102-MII-16203 | SAI1000-01R | 3102-MII-16203 |  | 3102-Z-6211 | 3102-MII-16203 | Ток расплавного насоса второго преполим. 3102-P-6203B | Second Pre-Polymerizer Melt Pump 3102-P-6203B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6205 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 3 | [12 empty] | Запись в БД произведена
464 | 3102 | Сombined Title | 3102-PZIA-62012A | SAI1000-01R | 3102-PZIA-62012A |  | 3102-Z-6210, 3102-Z-6211 | 3102-PZT-62012A | Р на входе 3102-R-6203 | 3102-R-6203 inlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6206 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,3 | 1,45 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C179/3000-S-MC-B02 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C179 |  |  | 3102-PZT-62012A/3102-S-JB-C179 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 2 | [12 empty] | Запись в БД произведена
465 | 3102 | Сombined Title | 3102-PZIA-62012B | SAI1000-01R | 3102-PZIA-62012B |  | 3102-Z-6210, 3102-Z-6211 | 3102-PZT-62012B | Р на входе 3102-R-6203 | 3102-R-6203 inlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6206 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,3 | 1,45 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C181/3000-S-MC-B02 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C181 |  |  | 3102-PZT-62012B/3102-S-JB-C181 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 2 | [12 empty] | Запись в БД произведена
466 | 3102 | Сombined Title | 3102-PZIA-62012C | SAI1000-01R | 3102-PZIA-62012C |  | 3102-Z-6210, 3102-Z-6211 | 3102-PZT-62012C | Р на входе 3102-R-6203 | 3102-R-6203 inlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6206 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,3 | 1,45 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C182/3000-S-MC-B03 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C182 |  |  | 3102-PZT-62012C/3102-S-JB-C182 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 3 | [12 empty] | Запись в БД произведена
468 | 3102 | 3102 | 3102-PZIA-62015A | SAI1000-01R | 3102-PZIA-62015A |  | 3102-Z-6212, 3102-Z-6213 | 3102-PZT-62015A | Р нагнетания 3102-P-6205A/B | 3102-P-6205A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6206 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-PZT-62015A/3102-S-JB-C138 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 0 | [12 empty] | Запись в БД произведена
469 | 3102 | 3102 | 3102-PZIA-62015B | SAI1000-01R | 3102-PZIA-62015B |  | 3102-Z-6212, 3102-Z-6213 | 3102-PZT-62015B | Р нагнетания 3102-P-6205A/B | 3102-P-6205A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6206 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-PZT-62015B/3102-S-JB-C139 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 0 | [12 empty] | Запись в БД произведена
470 | 3102 | 3102 | 3102-PZIA-62015C | SAI1000-01R | 3102-PZIA-62015C |  | 3102-Z-6212, 3102-Z-6213 | 3102-PZT-62015C | Р нагнетания 3102-P-6205A/B | 3102-P-6205A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6206 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C148/3000-S-MC-B03 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C148 |  |  | 3102-PZT-62015C/3102-S-JB-C148 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 4 | [12 empty] | Запись в БД произведена
472 | 3102 | Сombined Title | 3102-XZV-62061 | SKLPD0021-00 | 3102-XZV-62061 |  |  | 3102-XZV-62061 | PS к 3102-R-6202, отсечка подачи | PS to 3102-R-6202 cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6206 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
473 | 3102 | Сombined Title | 3102-XZV-62061 | SKLPD0021-00 | 3102-XZV-62061 |  | 3102-Z-6291 | 3102-XZY-62061 | PS к 3102-R-6202, отсечка подачи | PS to 3102-R-6202 cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6206 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR08 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3102-XZY-62061/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 5 | [12 empty] | Запись в БД произведена
474 | 3102 | Сombined Title | 3102-XZV-62061 | SKLPD0021-00 | 3102-XZV-62061 |  |  | 3102-XZZSC-62061 | PS к 3102-R-6202, отсечка подачи (закрыт) | PS to 3102-R-6202 cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6206 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C174/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 450 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C174 |  |  | 3102-XZZSC-62061/3102-S-JB-C174 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 19 | [12 empty] | Запись в БД произведена
475 | 3102 | Сombined Title | 3102-XZV-62061 | SKLPD0021-00 | 3102-XZV-62061 |  |  | 3102-XZZSO-62061 | PS к 3102-R-6202, отсечка подачи (открыт) | PS to 3102-R-6202 cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6206 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C174/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 450 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C174 |  |  | 3102-XZZSO-62061/3102-S-JB-C174 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 20 | [12 empty] | Запись в БД произведена
477 | 2202 | 3102 | 3102-MXI-76203A | SDO0001-01 | 3102-MXI-76203A |  | 3102-Z-6290 | 3102-MXI-76203A | SIS стоп мешалки первого полимеризатора 3102-AG-6203 | First Polymerizer Agitator 3102-AG-6203 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6206 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 18 | [12 empty] | Запись в БД произведена
479 | 2202 | 3102 | 3102-MXI-06205A | SDO0001-01 | 3102-MXI-06205A |  | 3102-Z-6212, 3102-Z-6290 | 3102-MXI-06205A | SIS стоп расплавного насоса первого полимеризатора 3102-P-6205A | First Polymerizer Melt Pump 3102-P-6205A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6206 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 6 | [12 empty] | Запись в БД произведена
480 | 2202 | 3102 | 3102-MII-06205 | SAI1000-01R | 3102-MII-06205 |  | 3102-Z-6212 | 3102-MII-06205 | Ток расплавного насоса первого полимеризатора 3102-P-6205A | First Polymerizer Melt Pump 3102-P-6205A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6206 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 4 | [12 empty] | Запись в БД произведена
482 | 2202 | 3102 | 3102-MXI-16205A | SDO0001-01 | 3102-MXI-16205A |  | 3102-Z-6213, 3102-Z-6290 | 3102-MXI-16205A | SIS стоп расплавного насоса первого полимеризатора 3102-P-6205B | First Polymerizer Melt Pump 3102-P-6205B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6206 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 13 | [12 empty] | Запись в БД произведена
483 | 2202 | 3102 | 3102-MII-16205 | SAI1000-01R | 3102-MII-16205 |  | 3102-Z-6213 | 3102-MII-16205 | Ток расплавного насоса первого полимеризатора 3102-P-6205B | First Polymerizer Melt Pump 3102-P-6205B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6206 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 5 | [12 empty] | Запись в БД произведена
485 | 3102 | 3102 | 3102-PZIA-62016A | SAI1000-01R | 3102-PZIA-62016A |  | 3102-Z-6212, 3102-Z-6213 | 3102-PZT-62016A | Р на входе 3102-R-6204 | 3102-R-6204 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C179/3000-S-MC-B02 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C179 |  |  | 3102-PZT-62016A/3102-S-JB-C179 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 0 | [12 empty] | Запись в БД произведена
486 | 3102 | 3102 | 3102-PZIA-62016B | SAI1000-01R | 3102-PZIA-62016B |  | 3102-Z-6212, 3102-Z-6213 | 3102-PZT-62016B | Р на входе 3102-R-6204 | 3102-R-6204 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C181/3000-S-MC-B02 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C181 |  |  | 3102-PZT-62016B/3102-S-JB-C181 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 12 | [12 empty] | Запись в БД произведена
487 | 3102 | 3102 | 3102-PZIA-62016C | SAI1000-01R | 3102-PZIA-62016C |  | 3102-Z-6212, 3102-Z-6213 | 3102-PZT-62016C | Р на входе 3102-R-6204 | 3102-R-6204 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C182/3000-S-MC-B03 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C182 |  |  | 3102-PZT-62016C/3102-S-JB-C182 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 8 | [12 empty] | Запись в БД произведена
489 | 3102 | 3102 | 3102-PZIA-62019A | SAI1000-01R | 3102-PZIA-62019A |  | 3102-Z-6214, 3102-Z-6215 | 3102-PZT-62019A | Р нагнетания 3102-P-6206A/B | 3102-P-6206A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-PZT-62019A/3102-S-JB-C138 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 1 | [12 empty] | Запись в БД произведена
490 | 3102 | 3102 | 3102-PZIA-62019B | SAI1000-01R | 3102-PZIA-62019B |  | 3102-Z-6214, 3102-Z-6215 | 3102-PZT-62019B | Р нагнетания 3102-P-6206A/B | 3102-P-6206A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-PZT-62019B/3102-S-JB-C139 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 1 | [12 empty] | Запись в БД произведена
491 | 3102 | 3102 | 3102-PZIA-62019C | SAI1000-01R | 3102-PZIA-62019C |  | 3102-Z-6214, 3102-Z-6215 | 3102-PZT-62019C | Р нагнетания 3102-P-6206A/B | 3102-P-6206A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C148/3000-S-MC-B03 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C148 |  |  | 3102-PZT-62019C/3102-S-JB-C148 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 5 | [12 empty] | Запись в БД произведена
493 | 2202 | 3102 | 3102-MXI-76204A | SDO0001-01 | 3102-MXI-76204A |  | 3102-Z-6290 | 3102-MXI-76204A | SIS стоп мешалки второго полимеризатора 3102-AG-6204 | Second Polymerizer Agitator 3102-AG-6204 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6207 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 19 | [12 empty] | Запись в БД произведена
495 | 2202 | 3102 | 3102-MXI-06206A | SDO0001-01 | 3102-MXI-06206A |  | 3102-Z-6214, 3102-Z-6290 | 3102-MXI-06206A | SIS стоп расплавного насоса второго полимеризатора 3102-P-6206A | Second Polymerizer Melt Pump 3102-P-6206A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6207 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 7 | [12 empty] | Запись в БД произведена
496 | 2202 | 3102 | 3102-MII-06206 | SAI1000-01R | 3102-MII-06206 |  | 3102-Z-6214 | 3102-MII-06206 | Ток расплавного насоса второго полимеризатора 3102-P-6206A | Second Polymerizer Melt Pump 3102-P-6206A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6207 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 6 | [12 empty] | Запись в БД произведена
498 | 2202 | 3102 | 3102-MXI-16206A | SDO0001-01 | 3102-MXI-16206A |  | 3102-Z-6215, 3102-Z-6290 | 3102-MXI-16206A | SIS стоп расплавного насоса второго полимеризатора 3102-P-6206B | Second Polymerizer Melt Pump 3102-P-6206B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6207 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 14 | [12 empty] | Запись в БД произведена
499 | 2202 | 3102 | 3102-MII-16206 | SAI1000-01R | 3102-MII-16206 |  | 3102-Z-6215 | 3102-MII-16206 | Ток расплавного насоса второго полимеризатора 3102-P-6206B | Second Polymerizer Melt Pump 3102-P-6206B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6207 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 7 | [12 empty] | Запись в БД произведена
501 | 3102 | 3102 | 3102-PZIA-62020A | SAI1000-01R | 3102-PZIA-62020A |  | 3102-Z-6214, 3102-Z-6215 | 3102-PZT-62020A | Р на входе 3102-R-6205 | 3102-R-6205 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C179/3000-S-MC-B02 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 434 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C179 |  |  | 3102-PZT-62020A/3102-S-JB-C179 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 1 | [12 empty] | Запись в БД произведена
502 | 3102 | 3102 | 3102-PZIA-62020B | SAI1000-01R | 3102-PZIA-62020B |  | 3102-Z-6214, 3102-Z-6215 | 3102-PZT-62020B | Р на входе 3102-R-6205 | 3102-R-6205 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C181/3000-S-MC-B02 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C181 |  |  | 3102-PZT-62020B/3102-S-JB-C181 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 13 | [12 empty] | Запись в БД произведена
503 | 3102 | 3102 | 3102-PZIA-62020C | SAI1000-01R | 3102-PZIA-62020C |  | 3102-Z-6214, 3102-Z-6215 | 3102-PZT-62020C | Р на входе 3102-R-6205 | 3102-R-6205 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C182/3000-S-MC-B03 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C182 |  |  | 3102-PZT-62020C/3102-S-JB-C182 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 9 | [12 empty] | Запись в БД произведена
505 | 3102 | 3102 | 3102-PZIA-62023A | SAI1000-01R | 3102-PZIA-62023A |  | 3102-Z-6216 | 3102-PZT-62023A | Р нагнетания 3102-P-6207A | 3102-P-6207A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-PZT-62023A/3102-S-JB-C138 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 2 | [12 empty] | Запись в БД произведена
506 | 3102 | 3102 | 3102-PZIA-62023B | SAI1000-01R | 3102-PZIA-62023B |  | 3102-Z-6216 | 3102-PZT-62023B | Р нагнетания 3102-P-6207A | 3102-P-6207A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-PZT-62023B/3102-S-JB-C139 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 2 | [12 empty] | Запись в БД произведена
507 | 3102 | 3102 | 3102-PZIA-62023C | SAI1000-01R | 3102-PZIA-62023C |  | 3102-Z-6216 | 3102-PZT-62023C | Р нагнетания 3102-P-6207A | 3102-P-6207A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C148/3000-S-MC-B03 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C148 |  |  | 3102-PZT-62023C/3102-S-JB-C148 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 6 | [12 empty] | Запись в БД произведена
509 | 3102 | 3102 | 3102-PZIA-62024A | SAI1000-01R | 3102-PZIA-62024A |  | 3102-Z-6217 | 3102-PZT-62024A | Р нагнетания 3102-P-6207B | 3102-P-6207B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C138/3000-S-MC-B02 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C138 |  |  | 3102-PZT-62024A/3102-S-JB-C138 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 3 | [12 empty] | Запись в БД произведена
510 | 3102 | 3102 | 3102-PZIA-62024B | SAI1000-01R | 3102-PZIA-62024B |  | 3102-Z-6217 | 3102-PZT-62024B | Р нагнетания 3102-P-6207B | 3102-P-6207B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C139/3000-S-MC-B02 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 509 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C139 |  |  | 3102-PZT-62024B/3102-S-JB-C139 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 3 | [12 empty] | Запись в БД произведена
511 | 3102 | 3102 | 3102-PZIA-62024C | SAI1000-01R | 3102-PZIA-62024C |  | 3102-Z-6217 | 3102-PZT-62024C | Р нагнетания 3102-P-6207B | 3102-P-6207B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C148/3000-S-MC-B03 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 499 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C148 |  |  | 3102-PZT-62024C/3102-S-JB-C148 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 7 | [12 empty] | Запись в БД произведена
513 | 3103 | Сombined Title | 3102-XZV-62081 | SKLPD0021-00 | 3102-XZV-62081 |  |  | 3102-XZV-62081 | PS к 3103-MX-6204, отсечка подачи | PS to 3103-MX-6204 cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6208 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
514 | 3103 | Сombined Title | 3102-XZV-62081 | SKLPD0021-00 | 3102-XZV-62081 |  | 3103-Z-6293 | 3102-XZY-62081 | PS к 3103-MX-6204, отсечка подачи | PS to 3103-MX-6204 cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6208 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR01 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3102-XZY-62081/3103-S-JB-D222 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 7 | [12 empty] | Запись в БД произведена
515 | 3103 | Сombined Title | 3102-XZV-62081 | SKLPD0021-00 | 3102-XZV-62081 |  |  | 3102-XZZSC-62081 | PS к 3103-MX-6204, отсечка подачи (закрыт) | PS to 3103-MX-6204 cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6208 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C220/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 504 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C220 |  |  | 3102-XZZSC-62081/3103-S-JB-C220 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 26 | [12 empty] | Запись в БД произведена
516 | 3103 | Сombined Title | 3102-XZV-62081 | SKLPD0021-00 | 3102-XZV-62081 |  |  | 3102-XZZSO-62081 | PS к 3103-MX-6204, отсечка подачи (открыт) | PS to 3103-MX-6204 cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6208 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C220/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 504 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C220 |  |  | 3102-XZZSO-62081/3103-S-JB-C220 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 27 | [12 empty] | Запись в БД произведена
518 | 2202 | 3102 | 3102-MXI-76205A | SDO0001-01 | 3102-MXI-76205A |  | 3102-Z-6290 | 3102-MXI-76205A | SIS стоп мешалки третьего полимеризатора 3102-AG-6205 | Third Polymerizer Agitator 3102-AG-6205 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6208 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 20 | [12 empty] | Запись в БД произведена
520 | 2202 | 3102 | 3102-MXI-06207A | SDO0001-01 | 3102-MXI-06207A |  | 3102-Z-6216, 3102-Z-6290 | 3102-MXI-06207A | SIS стоп расплавного насоса третьего полимеризатора 3102-P-6207A | Third Polymerizer Melt Pump 3102-P-6207A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6208 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 8 | [12 empty] | Запись в БД произведена
521 | 2202 | 3102 | 3102-MII-06207 | SAI1000-01R | 3102-MII-06207 |  | 3102-Z-6216 | 3102-MII-06207 | Ток расплавного насоса третьего полимеризатора 3102-P-6207A | Third Polymerizer Melt Pump 3102-P-6207A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6208 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 230 | A | 0 | 230 | A |  |  | 170 | 186 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 8 | [12 empty] | Запись в БД произведена
523 | 2202 | 3102 | 3102-MXI-16207A | SDO0001-01 | 3102-MXI-16207A |  | 3102-Z-6217, 3102-Z-6290 | 3102-MXI-16207A | SIS стоп расплавного насоса третьего полимеризатора 3102-P-6207B | Third Polymerizer Melt Pump 3102-P-6207B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6208 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S03 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 15 | [12 empty] | Запись в БД произведена
524 | 2202 | 3102 | 3102-MII-16207 | SAI1000-01R | 3102-MII-16207 |  | 3102-Z-6217 | 3102-MII-16207 | Ток расплавного насоса третьего полимеризатора 3102-P-6207B | Third Polymerizer Melt Pump 3102-P-6207B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6208 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 230 | A | 0 | 230 | A |  |  | 170 | 186 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 9 | [12 empty] | Запись в БД произведена
526 | 3103 | 3103 | 3103-PZIA-62026A | SAI1000-01R | 3103-PZIA-62026A |  | 3103-Z-6218 | 3103-PZT-62026A | Р нагнетания 3103-P-6208A | 3103-P-6208A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C200/3000-S-MC-B03 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C200 |  |  | 3103-PZT-62026A/3103-S-JB-C200 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 11 | [12 empty] | Запись в БД произведена
527 | 3103 | 3103 | 3103-PZIA-62026B | SAI1000-01R | 3103-PZIA-62026B |  | 3103-Z-6218 | 3103-PZT-62026B | Р нагнетания 3103-P-6208A | 3103-P-6208A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C208/3000-S-MC-B04 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C208 |  |  | 3103-PZT-62026B/3103-S-JB-C208 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 06 | - | A21-06 | - | A22-06 | - | 1 | [12 empty] | Запись в БД произведена
528 | 3103 | 3103 | 3103-PZIA-62026C | SAI1000-01R | 3103-PZIA-62026C |  | 3103-Z-6218 | 3103-PZT-62026C | Р нагнетания 3103-P-6208A | 3103-P-6208A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C209/3000-S-MC-B04 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 470 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C209 |  |  | 3103-PZT-62026C/3103-S-JB-C209 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 05 | - | A21-05 | - | A22-05 | - | 9 | [12 empty] | Запись в БД произведена
530 | 3103 | 3103 | 3103-PZIA-62027A | SAI1000-01R | 3103-PZIA-62027A |  | 3103-Z-6219 | 3103-PZT-62027A | Р нагнетания 3103-P-6208B | 3103-P-6208B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C200/3000-S-MC-B03 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C200 |  |  | 3103-PZT-62027A/3103-S-JB-C200 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 12 | [12 empty] | Запись в БД произведена
531 | 3103 | 3103 | 3103-PZIA-62027B | SAI1000-01R | 3103-PZIA-62027B |  | 3103-Z-6219 | 3103-PZT-62027B | Р нагнетания 3103-P-6208B | 3103-P-6208B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C208/3000-S-MC-B04 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C208 |  |  | 3103-PZT-62027B/3103-S-JB-C208 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 06 | - | A21-06 | - | A22-06 | - | 2 | [12 empty] | Запись в БД произведена
532 | 3103 | 3103 | 3103-PZIA-62027C | SAI1000-01R | 3103-PZIA-62027C |  | 3103-Z-6219 | 3103-PZT-62027C | Р нагнетания 3103-P-6208B | 3103-P-6208B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C209/3000-S-MC-B04 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 470 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C209 |  |  | 3103-PZT-62027C/3103-S-JB-C209 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 05 | - | A21-05 | - | A22-05 | - | 10 | [12 empty] | Запись в БД произведена
534 | 2202 | 3103 | 3103-MXI-06208A | SDO0001-01 | 3103-MXI-06208A |  | 3103-Z-6218, 3103-Z-6292 | 3103-MXI-06208A | SIS стоп расплавного насоса основного дегазатора 3103-P-6208A | Main Devolatilizer Melt Pump 3103-P-6208A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6209 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 21 | [12 empty] | Запись в БД произведена
535 | 2202 | 3103 | 3103-MII-06208 | SAI1000-01R | 3103-MII-06208 |  | 3103-Z-6218 | 3103-MII-06208 | Ток расплавного насоса основного дегазатора 3103-P-6208A | Main Devolatilizer Melt Pump 3103-P-6208A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6209 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 400 | A | 0 | 400 | A |  |  | 297 | 325 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 10 | [12 empty] | Запись в БД произведена
537 | 2202 | 3103 | 3103-MXI-16208A | SDO0001-01 | 3103-MXI-16208A |  | 3103-Z-6219, 3103-Z-6292 | 3103-MXI-16208A | SIS стоп расплавного насоса основного дегазатора 3103-P-6208B | Main Devolatilizer Melt Pump 3103-P-6208B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6209 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 30 | [12 empty] | Запись в БД произведена
538 | 2202 | 3103 | 3103-MII-16208 | SAI1000-01R | 3103-MII-16208 |  | 3103-Z-6219 | 3103-MII-16208 | Ток расплавного насоса основного дегазатора 3103-P-6208B | Main Devolatilizer Melt Pump 3103-P-6208B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6209 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 400 | A | 0 | 400 | A |  |  | 297 | 325 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 11 | [12 empty] | Запись в БД произведена
540 | 3103 | 3103 | 3103-PZIA-62030A | SAI1000-01R | 3103-PZIA-62030A |  | 3103-Z-6220 | 3103-PZT-62030A | Р нагнетания 3103-P-6209A | 3103-P-6209A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C200/3000-S-MC-B03 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C200 |  |  | 3103-PZT-62030A/3103-S-JB-C200 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 13 | [12 empty] | Запись в БД произведена
541 | 3103 | 3103 | 3103-PZIA-62030B | SAI1000-01R | 3103-PZIA-62030B |  | 3103-Z-6220 | 3103-PZT-62030B | Р нагнетания 3103-P-6209A | 3103-P-6209A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C208/3000-S-MC-B04 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C208 |  |  | 3103-PZT-62030B/3103-S-JB-C208 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 06 | - | A21-06 | - | A22-06 | - | 3 | [12 empty] | Запись в БД произведена
542 | 3103 | 3103 | 3103-PZIA-62030C | SAI1000-01R | 3103-PZIA-62030C |  | 3103-Z-6220 | 3103-PZT-62030C | Р нагнетания 3103-P-6209A | 3103-P-6209A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C209/3000-S-MC-B04 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 470 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C209 |  |  | 3103-PZT-62030C/3103-S-JB-C209 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 05 | - | A21-05 | - | A22-05 | - | 11 | [12 empty] | Запись в БД произведена
544 | 3103 | 3103 | 3103-PZIA-62031A | SAI1000-01R | 3103-PZIA-62031A |  | 3103-Z-6221 | 3103-PZT-62031A | Р нагнетания 3103-P-6209B | 3103-P-6209B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C200/3000-S-MC-B03 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C200 |  |  | 3103-PZT-62031A/3103-S-JB-C200 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 15 | [12 empty] | Запись в БД произведена
545 | 3103 | 3103 | 3103-PZIA-62031B | SAI1000-01R | 3103-PZIA-62031B |  | 3103-Z-6221 | 3103-PZT-62031B | Р нагнетания 3103-P-6209B | 3103-P-6209B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C208/3000-S-MC-B04 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C208 |  |  | 3103-PZT-62031B/3103-S-JB-C208 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 06 | - | A21-06 | - | A22-06 | - | 5 | [12 empty] | Запись в БД произведена
546 | 3103 | 3103 | 3103-PZIA-62031C | SAI1000-01R | 3103-PZIA-62031C |  | 3103-Z-6221 | 3103-PZT-62031C | Р нагнетания 3103-P-6209B | 3103-P-6209B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C209/3000-S-MC-B04 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 470 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C209 |  |  | 3103-PZT-62031C/3103-S-JB-C209 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 05 | - | A21-05 | - | A22-05 | - | 13 | [12 empty] | Запись в БД произведена
548 | 3103 | 3103 | 3103-TZIA-62045A | SAI1000-01R | 3103-TZIA-62045A |  | 3103-Z-6220 | 3103-TZT-62045A | Т на выходе 3103-P-6209A | 3103-P-6209A outlet temperature | Temperature Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C200/3000-S-MC-B03 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C200 |  |  | 3103-TZT-62045A/3103-S-JB-C200 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 14 | [12 empty] | Запись в БД произведена
549 | 3103 | 3103 | 3103-TZIA-62045B | SAI1000-01R | 3103-TZIA-62045B |  | 3103-Z-6220 | 3103-TZT-62045B | Т на выходе 3103-P-6209A | 3103-P-6209A outlet temperature | Temperature Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C208/3000-S-MC-B04 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C208 |  |  | 3103-TZT-62045B/3103-S-JB-C208 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 06 | - | A21-06 | - | A22-06 | - | 4 | [12 empty] | Запись в БД произведена
550 | 3103 | 3103 | 3103-TZIA-62045C | SAI1000-01R | 3103-TZIA-62045C |  | 3103-Z-6220 | 3103-TZT-62045C | Т на выходе 3103-P-6209A | 3103-P-6209A outlet temperature | Temperature Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C209/3000-S-MC-B04 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 470 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C209 |  |  | 3103-TZT-62045C/3103-S-JB-C209 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 05 | - | A21-05 | - | A22-05 | - | 12 | [12 empty] | Запись в БД произведена
552 | 3103 | 3103 | 3103-TZIA-62047A | SAI1000-01R | 3103-TZIA-62047A |  | 3103-Z-6221 | 3103-TZT-62047A | Т на выходе 3103-P-6209B | 3103-P-6209B outlet temperature | Temperature Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C200/3000-S-MC-B03 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C200 |  |  | 3103-TZT-62047A/3103-S-JB-C200 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 03 | - | A21-03 | - | A22-03 | - | 0 | [12 empty] | Запись в БД произведена
553 | 3103 | 3103 | 3103-TZIA-62047B | SAI1000-01R | 3103-TZIA-62047B |  | 3103-Z-6221 | 3103-TZT-62047B | Т на выходе 3103-P-6209B | 3103-P-6209B outlet temperature | Temperature Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C208/3000-S-MC-B04 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C208 |  |  | 3103-TZT-62047B/3103-S-JB-C208 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 06 | - | A21-06 | - | A22-06 | - | 6 | [12 empty] | Запись в БД произведена
554 | 3103 | 3103 | 3103-TZIA-62047C | SAI1000-01R | 3103-TZIA-62047C |  | 3103-Z-6221 | 3103-TZT-62047C | Т на выходе 3103-P-6209B | 3103-P-6209B outlet temperature | Temperature Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C209/3000-S-MC-B04 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 470 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C209 |  |  | 3103-TZT-62047C/3103-S-JB-C209 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 05 | - | A21-05 | - | A22-05 | - | 14 | [12 empty] | Запись в БД произведена
556 | 2202 | 3103 | 3103-MXI-06209A | SDO0001-01 | 3103-MXI-06209A |  | 3103-Z-6220, 3103-Z-6292 | 3103-MXI-06209A | SIS стоп расплавного насоса финального дегазатора 3103-P-6209A | Final Devolatilizer Melt Pump 3103-P-6209A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6210 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 22 | [12 empty] | Запись в БД произведена
557 | 2202 | 3103 | 3103-MII-06209 | SAI1000-01R | 3103-MII-06209 |  | 3103-Z-6220 | 3103-MII-06209 | Ток расплавного насоса финального дегазатора 3103-P-6209A | Final Devolatilizer Melt Pump 3103-P-6209A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6210 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 450 | A | 0 | 450 | A |  |  | 344 | 375 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 12 | [12 empty] | Запись в БД произведена
559 | 2202 | 3103 | 3103-MXI-16209A | SDO0001-01 | 3103-MXI-16209A |  | 3103-Z-6221, 3103-Z-6292 | 3103-MXI-16209A | SIS стоп расплавного насоса финального дегазатора 3103-P-6209B | Final Devolatilizer Melt Pump 3103-P-6209B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6210 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 31 | [12 empty] | Запись в БД произведена
560 | 2202 | 3103 | 3103-MII-16209 | SAI1000-01R | 3103-MII-16209 |  | 3103-Z-6221 | 3103-MII-16209 | Ток расплавного насоса финального дегазатора 3103-P-6209B | Final Devolatilizer Melt Pump 3103-P-6209B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6210 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 450 | A | 0 | 450 | A |  |  | 344 | 375 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 13 | [12 empty] | Запись в БД произведена
562 | 3103 | 3103 | 3103-LZSA-62010 | SDI0010-01R | 3103-LZSA-62010 |  | 3103-Z-6224 | 3103-LZS-62010 | Ур. на входе 3103-P-6210A | 3103-P-6210A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3103-LZS-62010/3103-S-JB-C211 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 10 | - | A21-10 | - | A22-10 | - | 6 | [12 empty] | Запись в БД произведена
564 | 3103 | 3103 | 3103-LZSA-62011 | SDI0010-01R | 3103-LZSA-62011 |  | 3103-Z-6224 | 3103-LZS-62011 | Ур. на входе 3103-P-6210B | 3103-P-6210B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3103-LZS-62011/3103-S-JB-C211 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 2 | [12 empty] | Запись в БД произведена
566 | 3103 | 3103 | 3103-XZV-62117 | SKLPD0021-00 | 3103-XZV-62117 |  |  | 3103-XZV-62117 | Вход 3103-P-6210 | 3103-P-6210 Inlet | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
567 | 3103 | 3103 | 3103-XZV-62117 | SKLPD0021-00 | 3103-XZV-62117 |  | 3103-Z-6240 | 3103-XZY-62117 | Вход 3103-P-6210 | 3103-P-6210 Inlet | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR11 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62117/3103-S-JB-D222 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 19 | [12 empty] | Запись в БД произведена
568 | 3103 | 3103 | 3103-XZV-62117 | SKLPD0021-00 | 3103-XZV-62117 |  |  | 3103-XZZSC-62117 | Вход 3103-P-6210 (закрыт) | 3103-P-6210 Inlet | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR13 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSC-62117/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 27 | [12 empty] | Запись в БД произведена
569 | 3103 | 3103 | 3103-XZV-62117 | SKLPD0021-00 | 3103-XZV-62117 |  |  | 3103-XZZSO-62117 | Вход 3103-P-6210 (открыт) | 3103-P-6210 Inlet | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR14 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSO-62117/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 0 | [12 empty] | Запись в БД произведена
571 | 3103 | 3103 | 3103-XZV-62118 | SKLPD0021-00 | 3103-XZV-62118 |  |  | 3103-XZV-62118 | Выход 3103-P-6210 | 3103-P-6210 Outlet | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
572 | 3103 | 3103 | 3103-XZV-62118 | SKLPD0021-00 | 3103-XZV-62118 |  | 3103-Z-6240 | 3103-XZY-62118 | Выход 3103-P-6210 | 3103-P-6210 Outlet | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR10 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62118/3103-S-JB-D222 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 20 | [12 empty] | Запись в БД произведена
573 | 3103 | 3103 | 3103-XZV-62118 | SKLPD0021-00 | 3103-XZV-62118 |  |  | 3103-XZZSC-62118 | Выход 3103-P-6210 (закрыт) | 3103-P-6210 Outlet | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSC-62118/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 28 | [12 empty] | Запись в БД произведена
574 | 3103 | 3103 | 3103-XZV-62118 | SKLPD0021-00 | 3103-XZV-62118 |  |  | 3103-XZZSO-62118 | Выход 3103-P-6210 (открыт) | 3103-P-6210 Outlet | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSO-62118/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 1 | [12 empty] | Запись в БД произведена
576 | 3103 | 3103 | 3103-PZIA-62045 | SAI1000-01R | 3103-PZIA-62045 |  | 3103-Z-6231 | 3103-PZT-62045 | Р на входе 3103-PK-6213A/B | 3103-PK-6213A/B inlet pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | kPaA | 0 | 6 | kPaA |  |  | 1 | 1,5 |  | kPaA | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-PZT-62045/3000-S-MC-B03 |  | NH-IA-DJYYP3 1x2x1.5 | 485 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B03 | Одиночный |  | 3103-PZT-62045/3000-S-MC-B03 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 03 | - | A21-03 | - | A22-03 | - | 5 | [12 empty] | Запись в БД произведена
578 | 3103 |  | 3103-XZV-62025 | SKLPD0021-00 | 3103-XZV-62025 |  |  | 3103-XZV-62025 | Поток N2 к 3103-PK-6213AB | N2 flow to 3103-PK-6213AB | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
579 | 3103 | 3103 | 3103-XZV-62025 | SKLPD0021-00 | 3103-XZV-62025 |  | 3103-Z-6231 | 3103-XZY-62025 | Поток N2 к 3103-PK-6213AB | N2 flow to 3103-PK-6213AB | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-XZY-62025/3000-S-MC-B14 |  | NH-KYJYP3 2x2.5 | 485 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B14 | Одиночный |  | 3103-XZY-62025/3000-S-MC-B14 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 12 | [12 empty] | Запись в БД произведена
580 | 3103 | 3103 | 3103-XZV-62025 | SKLPD0021-00 | 3103-XZV-62025 |  |  | 3103-XZZSC-62025 | Поток N2 к 3103-PK-6213AB (закрыт) | N2 flow to 3103-PK-6213AB | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-XZZSC-62025/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 485 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3103-XZZSC-62025/3000-S-MC-B08 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 19 | [12 empty] | Запись в БД произведена
581 | 3103 | 3103 | 3103-XZV-62025 | SKLPD0021-00 | 3103-XZV-62025 |  |  | 3103-XZZSO-62025 | Поток N2 к 3103-PK-6213AB (открыт) | N2 flow to 3103-PK-6213AB | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-XZZSO-62025/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 485 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3103-XZZSO-62025/3000-S-MC-B08 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 22 | [12 empty] | Запись в БД произведена
583 | 2202 | 3103 | 3103-MXI-06210A | SDO0001-01 | 3103-MXI-06210A |  | 3103-Z-6224, 3103-Z-6240, 3103-Z-6292 | 3103-MXI-06210A | SIS стоп насоса конденсата финального дегазатора 3103-P-6210A | Final Devolatilizer Condensate Pump 3103-P-6210A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6211 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 23 | [12 empty] | Запись в БД произведена
585 | 2202 | 3103 | 3103-MXI-16210A | SDO0001-01 | 3103-MXI-16210A |  | 3103-Z-6224, 3103-Z-6240, 3103-Z-6292 | 3103-MXI-16210A | SIS стоп насоса конденсата финального дегазатора 3103-P-6210B | Final Devolatilizer Condensate Pump 3103-P-6210B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6211 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 0 | [12 empty] | Запись в БД произведена
587 | 3103 | 3103 | 3103-LZSA-62033A | SDI0010-01R | 3103-LZSA-62033A |  | 3103-Z-6225 | 3103-LZS-62033A | Ур. на входе 3103-P-6211A | 3103-P-6211A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C198/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C198 |  |  | 3103-LZS-62033A/3103-S-JB-C198 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 23 | [12 empty] | Запись в БД произведена
589 | 3103 | 3103 | 3103-LZSA-62033B | SDI0010-01R | 3103-LZSA-62033B |  | 3103-Z-6225 | 3103-LZS-62033B | Ур. на входе 3103-P-6211B | 3103-P-6211B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C203/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C203 |  |  | 3103-LZS-62033B/3103-S-JB-C203 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 22 | [12 empty] | Запись в БД произведена
591 | 3103 | Сombined Title | 3103-XZV-62105 | SKLPD0021-00 | 3103-XZV-62105 |  |  | 3103-XZV-62105 | Вход 3103-P-6211AB | 3103-P-6211AB Inlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
592 | 3103 | Сombined Title | 3103-XZV-62105 | SKLPD0021-00 | 3103-XZV-62105 |  | 3103-Z-6241 | 3103-XZY-62105 | Вход 3103-P-6211AB | 3103-P-6211AB Inlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR01 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3103-XZY-62105/3103-S-JB-D213 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 28 | [12 empty] | Запись в БД произведена
593 | 3103 | Сombined Title | 3103-XZV-62105 | SKLPD0021-00 | 3103-XZV-62105 |  |  | 3103-XZZSC-62105 | Вход 3103-P-6211AB (закрыт) | 3103-P-6211AB Inlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3103-XZZSC-62105/3103-S-JB-C210 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 9 | [12 empty] | Запись в БД произведена
594 | 3103 | Сombined Title | 3103-XZV-62105 | SKLPD0021-00 | 3103-XZV-62105 |  |  | 3103-XZZSO-62105 | Вход 3103-P-6211AB (открыт) | 3103-P-6211AB Inlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3103-XZZSO-62105/3103-S-JB-C210 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 10 | [12 empty] | Запись в БД произведена
596 | 3103 | Сombined Title | 3103-XZV-62106 | SKLPD0021-00 | 3103-XZV-62106 |  |  | 3103-XZV-62106 | Выход 3103-P-6211AB | 3103-P-6211AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
597 | 3103 | Сombined Title | 3103-XZV-62106 | SKLPD0021-00 | 3103-XZV-62106 |  | 3103-Z-6241, 3103-Z-6293 | 3103-XZY-62106 | Выход 3103-P-6211AB | 3103-P-6211AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR02 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62106/3103-S-JB-D222 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 8 | [12 empty] | Запись в БД произведена
598 | 3103 | Сombined Title | 3103-XZV-62106 | SKLPD0021-00 | 3103-XZV-62106 |  |  | 3103-XZZSC-62106 | Выход 3103-P-6211AB (закрыт) | 3103-P-6211AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C220/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 504 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C220 |  |  | 3103-XZZSC-62106/3103-S-JB-C220 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 28 | [12 empty] | Запись в БД произведена
599 | 3103 | Сombined Title | 3103-XZV-62106 | SKLPD0021-00 | 3103-XZV-62106 |  |  | 3103-XZZSO-62106 | Выход 3103-P-6211AB (открыт) | 3103-P-6211AB Outlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C220/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 504 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C220 |  |  | 3103-XZZSO-62106/3103-S-JB-C220 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 31 | [12 empty] | Запись в БД произведена
601 | 3103 | 3103 | 3103-TZIA-66355A | SAI1000-01R | 3103-TZIA-66355A |  | 3103-Z-6241 | 3103-TZT-66355A | Т подшипника 3103-P-6211A | 3103-P-6211A Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ | REV 3 | Update P&ID No. |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C200/3000-S-MC-B03 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C200 |  |  | 3103-TZT-66355A/3103-S-JB-C200 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 4 | [12 empty] | Запись в БД произведена
602 | 2202 | 3103 | 3103-MXI-06211A | SDO0001-01 | 3103-MXI-06211A |  | 3103-Z-6225, 3103-Z-6241, 3103-Z-6292 | 3103-MXI-06211A | SIS стоп кубового насоса колонны очистки 3103-P-6211A | Purification Column Kettle Pump 3103-P-6211A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6212 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 24 | [12 empty] | Запись в БД произведена
604 | 3103 | 3103 | 3103-TZIA-66355B | SAI1000-01R | 3103-TZIA-66355B |  | 3103-Z-6241 | 3103-TZT-66355B | Т подшипника 3103-P-6211B | 3103-P-6211B Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6212 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ | REV 3 | Update P&ID No. |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C208/3000-S-MC-B04 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C208 |  |  | 3103-TZT-66355B/3103-S-JB-C208 | 3000-S-SC-B01 | 3000-S-MC-B04 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 8 | [12 empty] | Запись в БД произведена
605 | 2202 | 3103 | 3103-MXI-16211A | SDO0001-01 | 3103-MXI-16211A |  | 3103-Z-6225, 3103-Z-6241, 3103-Z-6292 | 3103-MXI-16211A | SIS стоп кубового насоса колонны очистки 3103-P-6211B | Purification Column Kettle Pump 3103-P-6211B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6212 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 1 | [12 empty] | Запись в БД произведена
607 | 3103 | 3103 | 3103-LZSA-62034A | SDI0010-01R | 3103-LZSA-62034A |  | 3103-Z-6226 | 3103-LZS-62034A | Ур. на входе 3103-P-6212A | 3103-P-6212A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C198/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C198 |  |  | 3103-LZS-62034A/3103-S-JB-C198 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 12 | [12 empty] | Запись в БД произведена
609 | 3103 | 3103 | 3103-LZSA-62034B | SDI0010-01R | 3103-LZSA-62034B |  | 3103-Z-6226 | 3103-LZS-62034B | Ур. на входе 3103-P-6212B | 3103-P-6212B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C203/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C203 |  |  | 3103-LZS-62034B/3103-S-JB-C203 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 17 | [12 empty] | Запись в БД произведена
611 | 3103 | Сombined Title | 3103-XZV-62107 | SKLPD0021-00 | 3103-XZV-62107 |  |  | 3103-XZV-62107 | Вход 3103-P-6212AB | 3103-P-6212AB Inlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6213 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
612 | 3103 | Сombined Title | 3103-XZV-62107 | SKLPD0021-00 | 3103-XZV-62107 |  | 3103-Z-6242 | 3103-XZY-62107 | Вход 3103-P-6212AB | 3103-P-6212AB Inlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6213 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR03 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62107/3103-S-JB-D222 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 9 | [12 empty] | Запись в БД произведена
613 | 3103 | Сombined Title | 3103-XZV-62107 | SKLPD0021-00 | 3103-XZV-62107 |  |  | 3103-XZZSC-62107 | Вход 3103-P-6212AB (закрыт) | 3103-P-6212AB Inlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C220/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 504 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C220 |  |  | 3103-XZZSC-62107/3103-S-JB-C220 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 29 | [12 empty] | Запись в БД произведена
614 | 3103 | Сombined Title | 3103-XZV-62107 | SKLPD0021-00 | 3103-XZV-62107 |  |  | 3103-XZZSO-62107 | Вход 3103-P-6212AB (открыт) | 3103-P-6212AB Inlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C220/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 504 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C220 |  |  | 3103-XZZSO-62107/3103-S-JB-C220 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 12 | [12 empty] | Запись в БД произведена
616 | 3103 | Сombined Title | 3103-XZV-62108 | SKLPD0021-00 | 3103-XZV-62108 |  |  | 3103-XZV-62108 | Выход 3103-P-6212AB | 3103-P-6212AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6213 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
617 | 3103 | Сombined Title | 3103-XZV-62108 | SKLPD0021-00 | 3103-XZV-62108 |  | 3103-Z-6242, 3103-Z-6293 | 3103-XZY-62108 | Выход 3103-P-6212AB | 3103-P-6212AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6213 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR04 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62108/3103-S-JB-D222 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 10 | [12 empty] | Запись в БД произведена
618 | 3103 | Сombined Title | 3103-XZV-62108 | SKLPD0021-00 | 3103-XZV-62108 |  |  | 3103-XZZSC-62108 | Выход 3103-P-6212AB (закрыт) | 3103-P-6212AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C220/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 504 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C220 |  |  | 3103-XZZSC-62108/3103-S-JB-C220 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 30 | [12 empty] | Запись в БД произведена
619 | 3103 | Сombined Title | 3103-XZV-62108 | SKLPD0021-00 | 3103-XZV-62108 |  |  | 3103-XZZSO-62108 | Выход 3103-P-6212AB (открыт) | 3103-P-6212AB Outlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C220/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 504 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C220 |  |  | 3103-XZZSO-62108/3103-S-JB-C220 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 12 | - | A11-12 | - | A12-12 | - | 13 | [12 empty] | Запись в БД произведена
621 | 3103 | 3103 | 3103-PZIA-62046 | SAI1000-01R | 3103-PZIA-62046 |  | 3103-Z-6232 | 3103-PZT-62046 | Р на выходе VG из 3103-E-6207 | 3103-E-6207 outlet pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6213 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | kPaA | 0 | 6 | kPaA |  |  | 4 | 5 |  | kPaA | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-PZT-62046/3000-S-MC-B03 |  | NH-IA-DJYYP3 1x2x1.5 | 485 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B03 | Одиночный |  | 3103-PZT-62046/3000-S-MC-B03 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 03 | - | A21-03 | - | A22-03 | - | 6 | [12 empty] | Запись в БД произведена
623 | 3103 |  | 3103-XZV-62026 | SKLPD0021-00 | 3103-XZV-62026 |  |  | 3103-XZV-62026 | Поток N2 к 3103-PK-6213AB | N2 flow to 3103-PK-6213AB | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6213 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
624 | 3103 | 3103 | 3103-XZV-62026 | SKLPD0021-00 | 3103-XZV-62026 |  | 3103-Z-6232 | 3103-XZY-62026 | Поток N2 к 3103-PK-6213AB | N2 flow to 3103-PK-6213AB | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6213 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-XZY-62026/3000-S-MC-B14 |  | NH-KYJYP3 2x2.5 | 485 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B14 | Одиночный |  | 3103-XZY-62026/3000-S-MC-B14 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 13 | [12 empty] | Запись в БД произведена
625 | 3103 | 3103 | 3103-XZV-62026 | SKLPD0021-00 | 3103-XZV-62026 |  |  | 3103-XZZSC-62026 | Поток N2 к 3103-PK-6213AB (закрыт) | N2 flow to 3103-PK-6213AB | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-XZZSC-62026/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 485 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3103-XZZSC-62026/3000-S-MC-B08 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 20 | [12 empty] | Запись в БД произведена
626 | 3103 | 3103 | 3103-XZV-62026 | SKLPD0021-00 | 3103-XZV-62026 |  |  | 3103-XZZSO-62026 | Поток N2 к 3103-PK-6213AB (открыт) | N2 flow to 3103-PK-6213AB | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-XZZSO-62026/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 485 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3103-XZZSO-62026/3000-S-MC-B08 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 23 | [12 empty] | Запись в БД произведена
628 | 2202 | 3103 | 3103-MXI-06212A | SDO0001-01 | 3103-MXI-06212A |  | 3103-Z-6226, 3103-Z-6242, 3103-Z-6292 | 3103-MXI-06212A | SIS стоп насоса рецикла колонны очистки 3103-P-6212A | Purification Column Kettle Pump 3103-P-6212A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6213 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 25 | [12 empty] | Запись в БД произведена
630 | 2202 | 3103 | 3103-MXI-16212A | SDO0001-01 | 3103-MXI-16212A |  | 3103-Z-6226, 3103-Z-6242, 3103-Z-6292 | 3103-MXI-16212A | SIS стоп насоса рецикла колонны очистки 3103-P-6212B | Purification Column Kettle Pump 3103-P-6212B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6213 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 2 | [12 empty] | Запись в БД произведена
632 | 3102 | 3102 | 3102-PZIA-62047 | SAI1000-01R | 3102-PZIA-62047 |  | 3103-Z-6233 | 3102-PZT-62047 | Р на входе 3103-PK-6215 | 3103-PK-6215 inlet pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6214 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 150 | kPaA | 0 | 150 | kPaA |  |  | 60 | 80 |  | kPaA | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-C181/3000-S-MC-B02 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 434 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C181 |  |  | 3102-PZT-62047/3102-S-JB-C181 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 14 | [12 empty] | Запись в БД произведена
634 | 3102 |  | 3103-XZV-62030 | SKLPD0021-00 | 3103-XZV-62030 |  |  | 3103-XZV-62030 | Поток N2 к 3103-PK-6215 | N2 flow to 3103-PK-6215 | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6214 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
635 | 3102 | 3102 | 3103-XZV-62030 | SKLPD0021-00 | 3103-XZV-62030 |  | 3103-Z-6233 | 3103-XZY-62030 | Поток N2 к 3103-PK-6215 | N2 flow to 3103-PK-6215 | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6214 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3102-S-JB-D195/3000-S-MC-B11 | PR06 | NH-KYJYP3 16x2.5 | 426 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D195 |  |  | 3103-XZY-62030/3102-S-JB-D195 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 14 | [12 empty] | Запись в БД произведена
636 | 3102 | 3102 | 3103-XZV-62030 | SKLPD0021-00 | 3103-XZV-62030 |  |  | 3103-XZZSC-62030 | Поток N2 к 3103-PK-6215 (закрыт) | N2 flow to 3103-PK-6215 | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6214 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-XZZSC-62030/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 462 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3103-XZZSC-62030/3000-S-MC-B08 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 21 | [12 empty] | Запись в БД произведена
637 | 3102 | 3102 | 3103-XZV-62030 | SKLPD0021-00 | 3103-XZV-62030 |  |  | 3103-XZZSO-62030 | Поток N2 к 3103-PK-6215 (открыт) | N2 flow to 3103-PK-6215 | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6214 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3103-XZZSO-62030/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 462 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3103-XZZSO-62030/3000-S-MC-B08 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 24 | [12 empty] | Запись в БД произведена
639 | 3103 | 3103 | 3103-LZSA-62037A | SDI0010-01R | 3103-LZSA-62037A |  | 3103-Z-6227 | 3103-LZS-62037A | Ур. на входе 3103-P-6218A | 3103-P-6218A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3103-LZS-62037A/3103-S-JB-C211 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 4 | [12 empty] | Запись в БД произведена
641 | 3103 | 3103 | 3103-LZSA-62037B | SDI0010-01R | 3103-LZSA-62037B |  | 3103-Z-6227 | 3103-LZS-62037B | Ур. на входе 3103-P-6218B | 3103-P-6218B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3103-LZS-62037B/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 27 | [12 empty] | Запись в БД произведена
643 | 3102 | Сombined Title | 3103-LZSA-62038A | SDI0010-01R | 3103-LZSA-62038A |  | 3103-Z-6228 | 3103-LZS-62038A | Ур. на входе 3103-P-6219A | 3103-P-6219A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3103-LZS-62038A/3102-S-JB-C142 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 6 | [12 empty] | Запись в БД произведена
645 | 3102 | Сombined Title | 3103-LZSA-62038B | SDI0010-01R | 3103-LZSA-62038B |  | 3103-Z-6228 | 3103-LZS-62038B | Ур. на входе 3103-P-6219B | 3103-P-6219B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3103-LZS-62038B/3102-S-JB-C143 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 8 | [12 empty] | Запись в БД произведена
647 | 3103 | Сombined Title | 3103-XZV-62113 | SKLPD0021-00 | 3103-XZV-62113 |  |  | 3103-XZV-62113 | Вход 3103-P-6218AB | 3103-P-6218AB Intlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
648 | 3103 | Сombined Title | 3103-XZV-62113 | SKLPD0021-00 | 3103-XZV-62113 |  | 3103-Z-6243 | 3103-XZY-62113 | Вход 3103-P-6218AB | 3103-P-6218AB Intlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR08 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62113/3103-S-JB-D222 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 11 | [12 empty] | Запись в БД произведена
649 | 3103 | Сombined Title | 3103-XZV-62113 | SKLPD0021-00 | 3103-XZV-62113 |  |  | 3103-XZZSC-62113 | Вход 3103-P-6218AB (закрыт) | 3103-P-6218AB Intlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSC-62113/3103-S-JB-C221 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 11 | [12 empty] | Запись в БД произведена
650 | 3103 | Сombined Title | 3103-XZV-62113 | SKLPD0021-00 | 3103-XZV-62113 |  |  | 3103-XZZSO-62113 | Вход 3103-P-6218AB (открыт) | 3103-P-6218AB Intlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSO-62113/3103-S-JB-C221 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 13 | [12 empty] | Запись в БД произведена
652 | 3103 | Сombined Title | 3103-XZV-62114 | SKLPD0021-00 | 3103-XZV-62114 |  |  | 3103-XZV-62114 | Выход 3103-P-6218AB | 3103-P-6218AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
653 | 3103 | Сombined Title | 3103-XZV-62114 | SKLPD0021-00 | 3103-XZV-62114 |  | 3103-Z-6243, 3103-Z-6293 | 3103-XZY-62114 | Выход 3103-P-6218AB | 3103-P-6218AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR09 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62114/3103-S-JB-D222 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 12 | [12 empty] | Запись в БД произведена
654 | 3103 | Сombined Title | 3103-XZV-62114 | SKLPD0021-00 | 3103-XZV-62114 |  |  | 3103-XZZSC-62114 | Выход 3103-P-6218AB (закрыт) | 3103-P-6218AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSC-62114/3103-S-JB-C221 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 12 | [12 empty] | Запись в БД произведена
655 | 3103 | Сombined Title | 3103-XZV-62114 | SKLPD0021-00 | 3103-XZV-62114 |  |  | 3103-XZZSO-62114 | Выход 3103-P-6218AB (открыт) | 3103-P-6218AB Outlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSO-62114/3103-S-JB-C221 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 06 | - | A11-06 | - | A12-06 | - | 14 | [12 empty] | Запись в БД произведена
657 | 3102 | Сombined Title | 3103-XZV-62115 | SKLPD0021-00 | 3103-XZV-62115 |  |  | 3103-XZV-62115 | Вход 3103-P-6219AB | 3103-P-6219AB Intlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
658 | 3102 | Сombined Title | 3103-XZV-62115 | SKLPD0021-00 | 3103-XZV-62115 |  | 3103-Z-6244 | 3103-XZY-62115 | Вход 3103-P-6219AB | 3103-P-6219AB Intlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D158/3000-S-MC-B12 | PR03 | NH-KYJYP3 16x2.5 | 473 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D158 |  |  | 3103-XZY-62115/3102-S-JB-D158 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 27 | [12 empty] | Запись в БД произведена
659 | 3102 | Сombined Title | 3103-XZV-62115 | SKLPD0021-00 | 3103-XZV-62115 |  |  | 3103-XZZSC-62115 | Вход 3103-P-6219AB (закрыт) | 3103-P-6219AB Intlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C156/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 446 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C156 |  |  | 3103-XZZSC-62115/3102-S-JB-C156 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 15 | [12 empty] | Запись в БД произведена
660 | 3102 | Сombined Title | 3103-XZV-62115 | SKLPD0021-00 | 3103-XZV-62115 |  |  | 3103-XZZSO-62115 | Вход 3103-P-6219AB (открыт) | 3103-P-6219AB Intlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C156/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 446 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C156 |  |  | 3103-XZZSO-62115/3102-S-JB-C156 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 07 | - | A11-07 | - | A12-07 | - | 16 | [12 empty] | Запись в БД произведена
662 | 3102 | Сombined Title | 3103-XZV-62029 | SKLPD0021-00 | 3103-XZV-62029 |  |  | 3103-XZV-62029 | Отс. клап. 3103-P-6219A/B к 3102-MX-6201 | 3103-P-6219A/B to 3102-MX-6201 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
663 | 3102 | Сombined Title | 3103-XZV-62029 | SKLPD0021-00 | 3103-XZV-62029 |  | 3102-Z-6201, 3103-Z-6244, 3103-Z-6293 | 3103-XZY-62029 | Отс. клап. 3103-P-6219A/B к 3102-MX-6201 | 3103-P-6219A/B to 3102-MX-6201 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D165/3000-S-MC-B13 | PR05 | NH-KYJYP3 37x2.5 | 443 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D165 |  |  | 3103-XZY-62029/3102-S-JB-D165 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 8 | [12 empty] | Запись в БД произведена
664 | 3102 | Сombined Title | 3103-XZV-62029 | SKLPD0021-00 | 3103-XZV-62029 |  |  | 3103-XZZSC-62029 | Отс. клап. 3103-P-6219A/B к 3102-MX-6201 (закрыт) | 3103-P-6219A/B to 3102-MX-6201 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3103-XZZSC-62029/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 18 | [12 empty] | Запись в БД произведена
665 | 3102 | Сombined Title | 3103-XZV-62029 | SKLPD0021-00 | 3103-XZV-62029 |  |  | 3103-XZZSO-62029 | Отс. клап. 3103-P-6219A/B к 3102-MX-6201 (открыт) | 3103-P-6219A/B to 3102-MX-6201 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C164/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C164 |  |  | 3103-XZZSO-62029/3102-S-JB-C164 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 19 | [12 empty] | Запись в БД произведена
667 | 3103 | Сombined Title | 3103-TZIA-66361A | SAI1000-01R | 3103-TZIA-66361A |  | 3103-Z-6243 | 3103-TZT-66361A | Т подшипника 3103-P-6218A | 3103-P-6218A Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C200/3000-S-MC-B03 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C200 |  |  | 3103-TZT-66361A/3103-S-JB-C200 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 5 | [12 empty] | Запись в БД произведена
668 | 2202 | 3103 | 3103-MXI-06218A | SDO0001-01 | 3103-MXI-06218A |  | 3103-Z-6227, 3103-Z-6243, 3103-Z-6292 | 3103-MXI-06218A | SIS стоп насоса упл. жидкости вакуума дегазации 3103-P-6218A | Devolatilization Vacuum Sealing Liquid Pump 3103-P-6218A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6215 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 28 | [12 empty] | Запись в БД произведена
670 | 3103 | Сombined Title | 3103-TZIA-66361B | SAI1000-01R | 3103-TZIA-66361B |  | 3103-Z-6243 | 3103-TZT-66361B | Т подшипника 3103-P-6218B | 3103-P-6218B Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 (SCS2->SCS1) | 2490157-3000-PR007-6215 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C208/3000-S-MC-B04 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C208 |  |  | 3103-TZT-66361B/3103-S-JB-C208 | 3000-S-SC-B01 | 3000-S-MC-B04 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 9 | [12 empty] | Запись в БД произведена
671 | 2202 | 3103 | 3103-MXI-16218A | SDO0001-01 | 3103-MXI-16218A |  | 3103-Z-6227, 3103-Z-6243, 3103-Z-6292 | 3103-MXI-16218A | SIS стоп насоса упл. жидкости вакуума дегазации 3103-P-6218B | Devolatilization Vacuum Sealing Liquid Pump 3103-P-6218B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6215 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 4 | [12 empty] | Запись в БД произведена
673 | 2202 | Сombined Title | 3103-MXI-06219A | SDO0001-01 | 3103-MXI-06219A |  | 3103-Z-6228, 3103-Z-6244, 3102-Z-6290 | 3103-MXI-06219A | SIS стоп насоса упл. жидкости вакуума преполим. 3103-P-6219A | Pre-Polymerizer Vacuum Sealing Liquid Pump 3103-P-6219A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6215 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 29 | [12 empty] | Запись в БД произведена
675 | 2202 | Сombined Title | 3103-MXI-16219A | SDO0001-01 | 3103-MXI-16219A |  | 3103-Z-6228, 3103-Z-6244, 3102-Z-6290 | 3103-MXI-16219A | SIS стоп насоса упл. жидкости вакуума преполим. 3103-P-6219B | Pre-Polymerizer Vacuum Sealing Liquid Pump 3103-P-6219B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6215 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 5 | [12 empty] | Запись в БД произведена
677 | 3103 | 3103 | 3103-LZSA-62036 | SDI0010-01R | 3103-LZSA-62036 |  | 3103-Z-6230 | 3103-LZS-62036 | Ур. на входе 3103-P-6217 | 3103-P-6217 Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3103-LZS-62036/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 26 | [12 empty] | Запись в БД произведена
679 | 3103 | 3103 | 3103-LZSA-62035A | SDI0010-01R | 3103-LZSA-62035A |  | 3103-Z-6229 | 3103-LZS-62035A | Ур. на входе 3103-P-6216A | 3103-P-6216A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3103-LZS-62035A/3103-S-JB-C211 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 3 | [12 empty] | Запись в БД произведена
681 | 3103 | 3103 | 3103-LZSA-62035B | SDI0010-01R | 3103-LZSA-62035B |  | 3103-Z-6229 | 3103-LZS-62035B | Ур. на входе 3103-P-6216B | 3103-P-6216B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3103-LZS-62035B/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 25 | [12 empty] | Запись в БД произведена
683 | 3103 | 3103 | 3103-XZV-62109 | SKLPD0021-00 | 3103-XZV-62109 |  |  | 3103-XZV-62109 | Вход 3103-P-6216AB | 3103-P-6216AB Intlet | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
684 | 3103 | 3103 | 3103-XZV-62109 | SKLPD0021-00 | 3103-XZV-62109 |  | 3103-Z-6245 | 3103-XZY-62109 | Вход 3103-P-6216AB | 3103-P-6216AB Intlet | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR05 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62109/3103-S-JB-D222 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 16 | [12 empty] | Запись в БД произведена
685 | 3103 | 3103 | 3103-XZV-62109 | SKLPD0021-00 | 3103-XZV-62109 |  |  | 3103-XZZSC-62109 | Вход 3103-P-6216AB (закрыт) | 3103-P-6216AB Intlet | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSC-62109/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 24 | [12 empty] | Запись в БД произведена
686 | 3103 | 3103 | 3103-XZV-62109 | SKLPD0021-00 | 3103-XZV-62109 |  |  | 3103-XZZSO-62109 | Вход 3103-P-6216AB (открыт) | 3103-P-6216AB Intlet | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSO-62109/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 29 | [12 empty] | Запись в БД произведена
688 | 3103 | 3103 | 3103-XZV-62110 | SKLPD0021-00 | 3103-XZV-62110 |  |  | 3103-XZV-62110 | Выход 3103-P-6216AB | 3103-P-6216AB Outlet | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
689 | 3103 | 3103 | 3103-XZV-62110 | SKLPD0021-00 | 3103-XZV-62110 |  | 3103-Z-6245 | 3103-XZY-62110 | Выход 3103-P-6216AB | 3103-P-6216AB Outlet | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR06 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62110/3103-S-JB-D222 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 17 | [12 empty] | Запись в БД произведена
690 | 3103 | 3103 | 3103-XZV-62110 | SKLPD0021-00 | 3103-XZV-62110 |  |  | 3103-XZZSC-62110 | Выход 3103-P-6216AB (закрыт) | 3103-P-6216AB Outlet | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSC-62110/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 25 | [12 empty] | Запись в БД произведена
691 | 3103 | 3103 | 3103-XZV-62110 | SKLPD0021-00 | 3103-XZV-62110 |  |  | 3103-XZZSO-62110 | Выход 3103-P-6216AB (открыт) | 3103-P-6216AB Outlet | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSO-62110/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 30 | [12 empty] | Запись в БД произведена
693 | 3103 | 3103 | 3103-XZV-62111 | SKLPD0021-00 | 3103-XZV-62111 |  |  | 3103-XZV-62111 | Вход 3103-P-6217 | 3103-P-6217 Intlet | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
694 | 3103 | 3103 | 3103-XZV-62111 | SKLPD0021-00 | 3103-XZV-62111 |  | 3103-Z-6246 | 3103-XZY-62111 | Вход 3103-P-6217 | 3103-P-6217 Intlet | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D222/3000-S-MC-B12 | PR07 | NH-KYJYP3 37x2.5 | 462 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D222 |  |  | 3103-XZY-62111/3103-S-JB-D222 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 18 | [12 empty] | Запись в БД произведена
695 | 3103 | 3103 | 3103-XZV-62111 | SKLPD0021-00 | 3103-XZV-62111 |  |  | 3103-XZZSC-62111 | Вход 3103-P-6217 (закрыт) | 3103-P-6217 Intlet | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSC-62111/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 26 | [12 empty] | Запись в БД произведена
696 | 3103 | 3103 | 3103-XZV-62111 | SKLPD0021-00 | 3103-XZV-62111 |  |  | 3103-XZZSO-62111 | Вход 3103-P-6217 (открыт) | 3103-P-6217 Intlet | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C221/3000-S-MC-B06 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 460 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C221 |  |  | 3103-XZZSO-62111/3103-S-JB-C221 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 31 | [12 empty] | Запись в БД произведена
698 | 3103 | 3103 | 3103-XZV-62112 | SKLPD0021-00 | 3103-XZV-62112 |  |  | 3103-XZV-62112 | Выход 3103-P-6217 | 3103-P-6217 Outlet | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
699 | 3103 | 3103 | 3103-XZV-62112 | SKLPD0021-00 | 3103-XZV-62112 |  | 3103-Z-6246 | 3103-XZY-62112 | Выход 3103-P-6217 | 3103-P-6217 Outlet | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-XZY-62112/3000-S-MC-B12 |  | NH-KYJYP3 2x2.5 | 449 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B12 | Одиночный |  | 3103-XZY-62112/3000-S-MC-B12 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 21 | [12 empty] | Запись в БД произведена
700 | 3103 | 3103 | 3103-XZV-62112 | SKLPD0021-00 | 3103-XZV-62112 |  |  | 3103-XZZSC-62112 | Выход 3103-P-6217 (закрыт) | 3103-P-6217 Outlet | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-XZZSC-62112/3000-S-MC-B06 |  | NH-IA-DJYYP3 1x2x1.5 | 449 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B06 | Одиночный |  | 3103-XZZSC-62112/3000-S-MC-B06 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 10 | - | A21-10 | - | A22-10 | - | 4 | [12 empty] | Запись в БД произведена
701 | 3103 | 3103 | 3103-XZV-62112 | SKLPD0021-00 | 3103-XZV-62112 |  |  | 3103-XZZSO-62112 | Выход 3103-P-6217 (открыт) | 3103-P-6217 Outlet | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-XZZSO-62112/3000-S-MC-B06 |  | NH-IA-DJYYP3 1x2x1.5 | 449 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B06 | Одиночный |  | 3103-XZZSO-62112/3000-S-MC-B06 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 10 | - | A21-10 | - | A22-10 | - | 5 | [12 empty] | Запись в БД произведена
703 | 3103 | 3103 | 3103-TZIA-66359 | SAI1000-01R | 3103-TZIA-66359 |  | 3103-Z-6246 | 3103-TZT-66359 | Т подшипника 3103-P-6217 | 3103-P-6217 Bearing temperature | Temperature Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C209/3000-S-MC-B04 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 470 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C209 |  |  | 3103-TZT-66359/3103-S-JB-C209 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 05 | - | A21-05 | - | A22-05 | - | 8 | [12 empty] | Запись в БД произведена
704 | 2202 | 3103 | 3103-MXI-06217A | SDO0001-01 | 3103-MXI-06217A |  | 3103-Z-6230, 3103-Z-6246, 3103-Z-6292 | 3103-MXI-06217A | SIS стоп масляного насоса сепаратора 3103-P-6217 | Separator Oil Pump 3103-P-6217 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6216 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 27 | [12 empty] | Запись в БД произведена
706 | 3103 | 3103 | 3103-TZIA-66357A | SAI1000-01R | 3103-TZIA-66357A |  | 3103-Z-6245 | 3103-TZT-66357A | Т подшипника 3103-P-6216A | 3103-P-6216A Bearing temperature | Temperature Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C200/3000-S-MC-B03 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C200 |  |  | 3103-TZT-66357A/3103-S-JB-C200 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 10 | [12 empty] | Запись в БД произведена
707 | 2202 | 3103 | 3103-MXI-06216A | SDO0001-01 | 3103-MXI-06216A |  | 3103-Z-6229, 3103-Z-6245, 3103-Z-6292 | 3103-MXI-06216A | SIS стоп насоса откачки маслянистой воды 3103-P-6216A | Oily Water Extraction Pump 3103-P-6216A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6216 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 04 | 05 | A70-04 | A70-05 | A71-04 | A71-05 | 26 | [12 empty] | Запись в БД произведена
709 | 3103 | 3103 | 3103-TZIA-66357B | SAI1000-01R | 3103-TZIA-66357B |  | 3103-Z-6245 | 3103-TZT-66357B | Т подшипника 3103-P-6216B | 3103-P-6216B Bearing temperature | Temperature Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6216 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3103-S-JB-C208/3000-S-MC-B04 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 464 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C208 |  |  | 3103-TZT-66357B/3103-S-JB-C208 | 3000-S-SC-B02 | 3000-S-MC-B04 |  | A21 | A22 | 06 | - | A21-06 | - | A22-06 | - | 0 | [12 empty] | Запись в БД произведена
710 | 2202 | 3103 | 3103-MXI-16216A | SDO0001-01 | 3103-MXI-16216A |  | 3103-Z-6229, 3103-Z-6245, 3103-Z-6292 | 3103-MXI-16216A | SIS стоп насоса откачки маслянистой воды 3103-P-6216B | Oily Water Extraction Pump 3103-P-6216B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6216 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 3 | [12 empty] | Запись в БД произведена
712 | 3107 | 3107 | 3608-XZV-64007 | SKLPD0021-00 | 3608-XZV-64007 |  |  | 3608-XZV-64007 | Управление паровой завесой (MS) | MS for Steam Curtain control | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
713 | 3107 | 3107 | 3608-XZV-64007 | SKLPD0021-00 | 3608-XZV-64007 |  | 3107-Z-6402 | 3608-XZY-64007 | Управление паровой завесой (MS) | MS for Steam Curtain control | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-D413/3000-S-MC-B14 | PR05 | NH-KYJYP3 16x2.5 | 436 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D413 |  |  | 3608-XZY-64007/3107-S-JB-D413 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 14 | [12 empty] | Запись в БД произведена
714 | 3107 | 3107 | 3608-XZV-64007 | SKLPD0021-00 | 3608-XZV-64007 |  |  | 3608-XZZSC-64007 | Управление паровой завесой (MS) (закрыт) | MS for Steam Curtain control | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3608-XZZSC-64007/3107-S-JB-C411 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 18 | [12 empty] | Запись в БД произведена
715 | 3107 | 3107 | 3608-XZV-64007 | SKLPD0021-00 | 3608-XZV-64007 |  |  | 3608-XZZSO-64007 | Управление паровой завесой (MS) (открыт) | MS for Steam Curtain control | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3608-XZZSO-64007/3107-S-JB-C411 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 19 | [12 empty] | Запись в БД произведена
717 | 2202 |  | 3107-MXI-06401A | SDO0001-01 | 3107-MXI-06401A |  | 3107-Z-6490 | 3107-MXI-06401A | SIS стоп воздушного охладителя горячего масла 3107-E-6401A | Warm HTF Cooler 3107-E-6401A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | New add | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 0 | [12 empty] | Запись в БД произведена
718 | 2202 |  | 3107-MXI-16401A | SDO0001-01 | 3107-MXI-16401A |  | 3107-Z-6490 | 3107-MXI-16401A | SIS стоп воздушного охладителя горячего масла 3107-E-6401B | Warm HTF Cooler 3107-E-6401B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | New add | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 1 | [12 empty] | Запись в БД произведена
719 | 2202 |  | 3107-MXI-26401A | SDO0001-01 | 3107-MXI-26401A |  | 3107-Z-6490 | 3107-MXI-26401A | SIS стоп воздушного охладителя горячего масла 3107-E-6401C | Warm HTF Cooler 3107-E-6401C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | New add | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 2 | [12 empty] | Запись в БД произведена
720 | 2202 |  | 3107-MXI-36401A | SDO0001-01 | 3107-MXI-36401A |  | 3107-Z-6490 | 3107-MXI-36401A | SIS стоп воздушного охладителя горячего масла 3107-E-6401D | Warm HTF Cooler 3107-E-6401D SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | New add | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 3 | [12 empty] | Запись в БД произведена
722 | 3107 | 3107 | 3107-LZIA-64001 | SAI1000-01R | 3107-LZIA-64001 |  | 3107-Z-6410 | 3107-LZT-64001 | Уровень в 3107-V-6402 | 3107-V-6402 Liquid level indication | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6402 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 3000 | mm | 0 | 100 | % | 4,666667 | 27,33333 |  |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C410/3000-S-MC-B03 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 436 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C410 |  |  | 3107-LZT-64001/3107-S-JB-C410 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 4 | [12 empty] | Запись в БД произведена
724 | 3102 | 3102 | 3107-LZSA-64104A | SDI0010-01R | 3107-LZSA-64104A |  | 3107-Z-6411 | 3107-LZS-64104A | Ур. на входе 3107-HOP-6404A | 3107-HOP-6404A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR13 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-LZS-64104A/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 26 | [12 empty] | Запись в БД произведена
726 | 3102 | 3102 | 3107-LZSA-64104B | SDI0010-01R | 3107-LZSA-64104B |  | 3107-Z-6411 | 3107-LZS-64104B | Ур. на входе 3107-HOP-6404B | 3107-HOP-6404B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR13 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-LZS-64104B/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 5 | [12 empty] | Запись в БД произведена
728 | 3102 | Сombined Title | 3107-XZV-64001 | SKLPD0021-00 | 3107-XZV-64001 |  |  | 3107-XZV-64001 | Отс. клап. HTF к 3107-HOP-6404 | HTF to 3107-HOP-6404 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
729 | 3102 | Сombined Title | 3107-XZV-64001 | SKLPD0021-00 | 3107-XZV-64001 |  | 3102-Z-6201 | 3107-XZY-64001 | Отс. клап. HTF к 3107-HOP-6404 | HTF to 3107-HOP-6404 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR03 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3107-XZY-64001/3102-S-JB-D157 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 22 | [12 empty] | Запись в БД произведена
730 | 3102 | Сombined Title | 3107-XZV-64001 | SKLPD0021-00 | 3107-XZV-64001 |  |  | 3107-XZZSC-64001 | Отс. клап. HTF к 3107-HOP-6404 (закрыт) | HTF to 3107-HOP-6404 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSC-64001/3102-S-JB-C154 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 18 | [12 empty] | Запись в БД произведена
731 | 3102 | Сombined Title | 3107-XZV-64001 | SKLPD0021-00 | 3107-XZV-64001 |  |  | 3107-XZZSO-64001 | Отс. клап. HTF к 3107-HOP-6404 (открыт) | HTF to 3107-HOP-6404 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSO-64001/3102-S-JB-C154 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 20 | [12 empty] | Запись в БД произведена
733 | 3102 | Сombined Title | 3107-XZV-64002 | SKLPD0021-00 | 3107-XZV-64002 |  |  | 3107-XZV-64002 | Отс. клап. HTF к 3107-HOP-6404 | HTF to 3107-HOP-6404 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
734 | 3102 | Сombined Title | 3107-XZV-64002 | SKLPD0021-00 | 3107-XZV-64002 |  | 3102-Z-6201 | 3107-XZY-64002 | Отс. клап. HTF к 3107-HOP-6404 | HTF to 3107-HOP-6404 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR04 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3107-XZY-64002/3102-S-JB-D157 | 3000-S-SC-B01 | 3000-S-MC-B14 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 23 | [12 empty] | Запись в БД произведена
735 | 3102 | Сombined Title | 3107-XZV-64002 | SKLPD0021-00 | 3107-XZV-64002 |  |  | 3107-XZZSC-64002 | Отс. клап. HTF к 3107-HOP-6404 (закрыт) | HTF to 3107-HOP-6404 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSC-64002/3102-S-JB-C154 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 19 | [12 empty] | Запись в БД произведена
736 | 3102 | Сombined Title | 3107-XZV-64002 | SKLPD0021-00 | 3107-XZV-64002 |  |  | 3107-XZZSO-64002 | Отс. клап. HTF к 3107-HOP-6404 (открыт) | HTF to 3107-HOP-6404 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSO-64002/3102-S-JB-C154 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 21 | [12 empty] | Запись в БД произведена
738 | 3107 | 3107 | 3107-XZV-64101 | SKLPD0021-00 | 3107-XZV-64101 |  |  | 3107-XZV-64101 | Отс. клап. на входе 3107-HOP-6403ABC | 3107-HOP-6403ABC Inlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
739 | 3107 | 3107 | 3107-XZV-64101 | SKLPD0021-00 | 3107-XZV-64101 |  | 3107-Z-6453 | 3107-XZY-64101 | Отс. клап. на входе 3107-HOP-6403ABC | 3107-HOP-6403ABC Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-D413/3000-S-MC-B14 | PR02 | NH-KYJYP3 16x2.5 | 436 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D413 |  |  | 3107-XZY-64101/3107-S-JB-D413 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 12 | [12 empty] | Запись в БД произведена
740 | 3107 | 3107 | 3107-XZV-64101 | SKLPD0021-00 | 3107-XZV-64101 |  |  | 3107-XZZSC-64101 | Отс. клап. на входе 3107-HOP-6403ABC (закрыт) | 3107-HOP-6403ABC Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3107-XZZSC-64101/3107-S-JB-C411 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 14 | [12 empty] | Запись в БД произведена
741 | 3107 | 3107 | 3107-XZV-64101 | SKLPD0021-00 | 3107-XZV-64101 |  |  | 3107-XZZSO-64101 | Отс. клап. на входе 3107-HOP-6403ABC (открыт) | 3107-HOP-6403ABC Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3107-XZZSO-64101/3107-S-JB-C411 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 16 | [12 empty] | Запись в БД произведена
743 | 3107 | 3107 | 3107-XZV-64102 | SKLPD0021-00 | 3107-XZV-64102 |  |  | 3107-XZV-64102 | Отс. клап. на выходе 3107-HOP-6403ABC | 3107-HOP-6403ABC Outlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
744 | 3107 | 3107 | 3107-XZV-64102 | SKLPD0021-00 | 3107-XZV-64102 |  | 3107-Z-6453 | 3107-XZY-64102 | Отс. клап. на выходе 3107-HOP-6403ABC | 3107-HOP-6403ABC Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-D413/3000-S-MC-B14 | PR03 | NH-KYJYP3 16x2.5 | 436 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D413 |  |  | 3107-XZY-64102/3107-S-JB-D413 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 13 | [12 empty] | Запись в БД произведена
745 | 3107 | 3107 | 3107-XZV-64102 | SKLPD0021-00 | 3107-XZV-64102 |  |  | 3107-XZZSC-64102 | Отс. клап. на выходе 3107-HOP-6403ABC (закрыт) | 3107-HOP-6403ABC Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3107-XZZSC-64102/3107-S-JB-C411 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 15 | [12 empty] | Запись в БД произведена
746 | 3107 | 3107 | 3107-XZV-64102 | SKLPD0021-00 | 3107-XZV-64102 |  |  | 3107-XZZSO-64102 | Отс. клап. на выходе 3107-HOP-6403ABC (открыт) | 3107-HOP-6403ABC Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C411/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C411 |  |  | 3107-XZZSO-64102/3107-S-JB-C411 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 17 | [12 empty] | Запись в БД произведена
748 | 3102 | 3102 | 3107-XZV-64103 | SKLPD0021-00 | 3107-XZV-64103 |  |  | 3107-XZV-64103 | Отс. клап. на входе 3107-HOP-6404AB | 3107-HOP-6404AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
749 | 3102 | 3102 | 3107-XZV-64103 | SKLPD0021-00 | 3107-XZV-64103 |  | 3107-Z-6454 | 3107-XZY-64103 | Отс. клап. на входе 3107-HOP-6404AB | 3107-HOP-6404AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR05 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3107-XZY-64103/3102-S-JB-D157 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 0 | [12 empty] | Запись в БД произведена
750 | 3102 | 3102 | 3107-XZV-64103 | SKLPD0021-00 | 3107-XZV-64103 |  |  | 3107-XZZSC-64103 | Отс. клап. на входе 3107-HOP-6404AB (закрыт) | 3107-HOP-6404AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSC-64103/3102-S-JB-C154 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 0 | [12 empty] | Запись в БД произведена
751 | 3102 | 3102 | 3107-XZV-64103 | SKLPD0021-00 | 3107-XZV-64103 |  |  | 3107-XZZSO-64103 | Отс. клап. на входе 3107-HOP-6404AB (открыт) | 3107-HOP-6404AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSO-64103/3102-S-JB-C154 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 2 | [12 empty] | Запись в БД произведена
753 | 3102 | 3102 | 3107-XZV-64104 | SKLPD0021-00 | 3107-XZV-64104 |  |  | 3107-XZV-64104 | Отс. клап. на выходе 3107-HOP-6404AB | 3107-HOP-6404AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
754 | 3102 | 3102 | 3107-XZV-64104 | SKLPD0021-00 | 3107-XZV-64104 |  | 3107-Z-6454 | 3107-XZY-64104 | Отс. клап. на выходе 3107-HOP-6404AB | 3107-HOP-6404AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D158/3000-S-MC-B12 | PR05 | NH-KYJYP3 16x2.5 | 473 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D158 |  |  | 3107-XZY-64104/3102-S-JB-D158 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 1 | [12 empty] | Запись в БД произведена
755 | 3102 | 3102 | 3107-XZV-64104 | SKLPD0021-00 | 3107-XZV-64104 |  |  | 3107-XZZSC-64104 | Отс. клап. на выходе 3107-HOP-6404AB (закрыт) | 3107-HOP-6404AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSC-64104/3102-S-JB-C154 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 1 | [12 empty] | Запись в БД произведена
756 | 3102 | 3102 | 3107-XZV-64104 | SKLPD0021-00 | 3107-XZV-64104 |  |  | 3107-XZZSO-64104 | Отс. клап. на выходе 3107-HOP-6404AB (открыт) | 3107-HOP-6404AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSO-64104/3102-S-JB-C154 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 3 | [12 empty] | Запись в БД произведена
758 | 2202 | 3107 | 3107-MXI-46403A | SDO0001-01 | 3107-MXI-46403A |  | 3107-Z-6410, 3107-Z-6453, 3107-Z-6490 | 3107-MXI-46403A | SIS стоп цирк. насоса горячего HTF 3107-HOP-6403A | Warm HTF Circulation Pump 3107-HOP-6403A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 13 | [12 empty] | Запись в БД произведена
760 | 2202 | 3107 | 3107-MXI-56403A | SDO0001-01 | 3107-MXI-56403A |  | 3107-Z-6410, 3107-Z-6453, 3107-Z-6490 | 3107-MXI-56403A | SIS стоп цирк. насоса горячего HTF 3107-HOP-6403B | Warm HTF Circulation Pump 3107-HOP-6403B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 5 | [12 empty] | Запись в БД произведена
762 | 2202 | 3107 | 3107-MXI-66403A | SDO0001-01 | 3107-MXI-66403A |  | 3107-Z-6410, 3107-Z-6453, 3107-Z-6490 | 3107-MXI-66403A | SIS стоп цирк. насоса горячего HTF 3107-HOP-6403C | Warm HTF Circulation Pump 3107-HOP-6403C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 29 | [12 empty] | Запись в БД произведена
764 | 2202 | 3102 | 3107-MXI-46404A | SDO0001-01 | 3107-MXI-46404A |  | 3107-Z-6411, 3107-Z-6454, 3102-Z-6290 | 3107-MXI-46404A | SIS стоп насоса HTF подогревателя сырья 3107-HOP-6404A | Feedstock Preheater HTF Pump 3107-HOP-6404A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 14 | [12 empty] | Запись в БД произведена
766 | 2202 | 3102 | 3107-MXI-56404A | SDO0001-01 | 3107-MXI-56404A |  | 3107-Z-6411, 3107-Z-64544, 3102-Z-6290 | 3107-MXI-56404A | SIS стоп насоса HTF подогревателя сырья 3107-HOP-6404B | Feedstock Preheater HTF Pump 3107-HOP-6404B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 6 | [12 empty] | Запись в БД произведена
768 | 3102 | 3102 | 3107-LZSA-64105A | SDI0010-01R | 3107-LZSA-64105A |  | 3107-Z-6412 | 3107-LZS-64105A | Ур. на входе 3107-HOP-6405A | 3107-HOP-6405A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C128/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 454 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C128 |  |  | 3107-LZS-64105A/3102-S-JB-C128 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 4 | [12 empty] | Запись в БД произведена
770 | 3102 | 3102 | 3107-LZSA-64105B | SDI0010-01R | 3107-LZSA-64105B |  | 3107-Z-6412 | 3107-LZS-64105B | Ур. на входе 3107-HOP-6405B | 3107-HOP-6405B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C129/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 448 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C129 |  |  | 3107-LZS-64105B/3102-S-JB-C129 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 9 | [12 empty] | Запись в БД произведена
772 | 3102 | 3102 | 3107-LZSA-64106A | SDI0010-01R | 3107-LZSA-64106A |  | 3107-Z-6413 | 3107-LZS-64106A | Ур. на входе 3107-HOP-6406A | 3107-HOP-6406A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C128/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 454 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C128 |  |  | 3107-LZS-64106A/3102-S-JB-C128 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 5 | [12 empty] | Запись в БД произведена
774 | 3102 | 3102 | 3107-LZSA-64106B | SDI0010-01R | 3107-LZSA-64106B |  | 3107-Z-6413 | 3107-LZS-64106B | Ур. на входе 3107-HOP-6406B | 3107-HOP-6406B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C129/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 448 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C129 |  |  | 3107-LZS-64106B/3102-S-JB-C129 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 10 | [12 empty] | Запись в БД произведена
776 | 3102 | Сombined Title | 3107-XZV-64003 | SKLPD0021-00 | 3107-XZV-64003 |  |  | 3107-XZV-64003 | Отс. клап. HTF к 3107-HOP-6406 | HTF to 3107-HOP-6406 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
777 | 3102 | Сombined Title | 3107-XZV-64003 | SKLPD0021-00 | 3107-XZV-64003 |  | 3102-Z-6207 | 3107-XZY-64003 | Отс. клап. HTF к 3107-HOP-6406 | HTF to 3107-HOP-6406 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR02 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3107-XZY-64003/3102-S-JB-D144 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 1 | [12 empty] | Запись в БД произведена
778 | 3102 | Сombined Title | 3107-XZV-64003 | SKLPD0021-00 | 3107-XZV-64003 |  |  | 3107-XZZSC-64003 | Отс. клап. HTF к 3107-HOP-6406 (закрыт) | HTF to 3107-HOP-6406 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSC-64003/3102-S-JB-C140 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 24 | [12 empty] | Запись в БД произведена
779 | 3102 | Сombined Title | 3107-XZV-64003 | SKLPD0021-00 | 3107-XZV-64003 |  |  | 3107-XZZSO-64003 | Отс. клап. HTF к 3107-HOP-6406 (открыт) | HTF to 3107-HOP-6406 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSO-64003/3102-S-JB-C140 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 28 | [12 empty] | Запись в БД произведена
781 | 3102 | Сombined Title | 3107-XZV-64004 | SKLPD0021-00 | 3107-XZV-64004 |  |  | 3107-XZV-64004 | Отс. клап. HTF к 3107-HOP-6406 | HTF to 3107-HOP-6406 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
782 | 3102 | Сombined Title | 3107-XZV-64004 | SKLPD0021-00 | 3107-XZV-64004 |  | 3102-Z-6207 | 3107-XZY-64004 | Отс. клап. HTF к 3107-HOP-6406 | HTF to 3107-HOP-6406 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR03 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3107-XZY-64004/3102-S-JB-D144 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 2 | [12 empty] | Запись в БД произведена
783 | 3102 | Сombined Title | 3107-XZV-64004 | SKLPD0021-00 | 3107-XZV-64004 |  |  | 3107-XZZSC-64004 | Отс. клап. HTF к 3107-HOP-6406 (закрыт) | HTF to 3107-HOP-6406 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSC-64004/3102-S-JB-C140 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 25 | [12 empty] | Запись в БД произведена
784 | 3102 | Сombined Title | 3107-XZV-64004 | SKLPD0021-00 | 3107-XZV-64004 |  |  | 3107-XZZSO-64004 | Отс. клап. HTF к 3107-HOP-6406 (открыт) | HTF to 3107-HOP-6406 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSO-64004/3102-S-JB-C140 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 29 | [12 empty] | Запись в БД произведена
786 | 3102 | Сombined Title | 3107-XZV-64005 | SKLPD0021-00 | 3107-XZV-64005 |  |  | 3107-XZV-64005 | Отс. клап. HTF к 3107-HOP-6405 | HTF to 3107-HOP-6405 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
787 | 3102 | Сombined Title | 3107-XZV-64005 | SKLPD0021-00 | 3107-XZV-64005 |  | 3102-Z-6202 | 3107-XZY-64005 | Отс. клап. HTF к 3107-HOP-6405 | HTF to 3107-HOP-6405 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR04 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3107-XZY-64005/3102-S-JB-D144 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 3 | [12 empty] | Запись в БД произведена
788 | 3102 | Сombined Title | 3107-XZV-64005 | SKLPD0021-00 | 3107-XZV-64005 |  |  | 3107-XZZSC-64005 | Отс. клап. HTF к 3107-HOP-6405 (закрыт) | HTF to 3107-HOP-6405 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSC-64005/3102-S-JB-C140 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 26 | [12 empty] | Запись в БД произведена
789 | 3102 | Сombined Title | 3107-XZV-64005 | SKLPD0021-00 | 3107-XZV-64005 |  |  | 3107-XZZSO-64005 | Отс. клап. HTF к 3107-HOP-6405 (открыт) | HTF to 3107-HOP-6405 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSO-64005/3102-S-JB-C140 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 30 | [12 empty] | Запись в БД произведена
791 | 3102 | Сombined Title | 3107-XZV-64006 | SKLPD0021-00 | 3107-XZV-64006 |  |  | 3107-XZV-64006 | Отс. клап. HTF к 3107-HOP-6405 | HTF to 3107-HOP-6405 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
792 | 3102 | Сombined Title | 3107-XZV-64006 | SKLPD0021-00 | 3107-XZV-64006 |  | 3102-Z-6202 | 3107-XZY-64006 | Отс. клап. HTF к 3107-HOP-6405 | HTF to 3107-HOP-6405 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR05 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3107-XZY-64006/3102-S-JB-D144 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 4 | [12 empty] | Запись в БД произведена
793 | 3102 | Сombined Title | 3107-XZV-64006 | SKLPD0021-00 | 3107-XZV-64006 |  |  | 3107-XZZSC-64006 | Отс. клап. HTF к 3107-HOP-6405 (закрыт) | HTF to 3107-HOP-6405 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSC-64006/3102-S-JB-C140 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 27 | [12 empty] | Запись в БД произведена
794 | 3102 | Сombined Title | 3107-XZV-64006 | SKLPD0021-00 | 3107-XZV-64006 |  |  | 3107-XZZSO-64006 | Отс. клап. HTF к 3107-HOP-6405 (открыт) | HTF to 3107-HOP-6405 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSO-64006/3102-S-JB-C140 | 3000-S-SC-B01 | 3000-S-MC-B06 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 31 | [12 empty] | Запись в БД произведена
796 | 3102 | 3102 | 3107-XZV-64105 | SKLPD0021-00 | 3107-XZV-64105 |  |  | 3107-XZV-64105 | Отс. клап. на входе 3107-HOP-6405AB | 3107-HOP-6405AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
797 | 3102 | 3102 | 3107-XZV-64105 | SKLPD0021-00 | 3107-XZV-64105 |  | 3107-Z-6455 | 3107-XZY-64105 | Отс. клап. на входе 3107-HOP-6405AB | 3107-HOP-6405AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR06 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3107-XZY-64105/3102-S-JB-D144 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 0 | [12 empty] | Запись в БД произведена
798 | 3102 | 3102 | 3107-XZV-64105 | SKLPD0021-00 | 3107-XZV-64105 |  |  | 3107-XZZSC-64105 | Отс. клап. на входе 3107-HOP-6405AB (закрыт) | 3107-HOP-6405AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSC-64105/3102-S-JB-C140 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 14 | [12 empty] | Запись в БД произведена
799 | 3102 | 3102 | 3107-XZV-64105 | SKLPD0021-00 | 3107-XZV-64105 |  |  | 3107-XZZSO-64105 | Отс. клап. на входе 3107-HOP-6405AB (открыт) | 3107-HOP-6405AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSO-64105/3102-S-JB-C140 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 17 | [12 empty] | Запись в БД произведена
801 | 3102 | 3102 | 3107-XZV-64106 | SKLPD0021-00 | 3107-XZV-64106 |  |  | 3107-XZV-64106 | Отс. клап. на выходе 3107-HOP-6405AB | 3107-HOP-6405AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
802 | 3102 | 3102 | 3107-XZV-64106 | SKLPD0021-00 | 3107-XZV-64106 |  | 3107-Z-6455 | 3107-XZY-64106 | Отс. клап. на выходе 3107-HOP-6405AB | 3107-HOP-6405AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR07 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3107-XZY-64106/3102-S-JB-D144 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 1 | [12 empty] | Запись в БД произведена
803 | 3102 | 3102 | 3107-XZV-64106 | SKLPD0021-00 | 3107-XZV-64106 |  |  | 3107-XZZSC-64106 | Отс. клап. на выходе 3107-HOP-6405AB (закрыт) | 3107-HOP-6405AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSC-64106/3102-S-JB-C140 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 15 | [12 empty] | Запись в БД произведена
804 | 3102 | 3102 | 3107-XZV-64106 | SKLPD0021-00 | 3107-XZV-64106 |  |  | 3107-XZZSO-64106 | Отс. клап. на выходе 3107-HOP-6405AB (открыт) | 3107-HOP-6405AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3107-XZZSO-64106/3102-S-JB-C141 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 22 | [12 empty] | Запись в БД произведена
806 | 3102 | 3102 | 3107-XZV-64107 | SKLPD0021-00 | 3107-XZV-64107 |  |  | 3107-XZV-64107 | Отс. клап. на входе 3107-HOP-6406AB | 3107-HOP-6406AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
807 | 3102 | 3102 | 3107-XZV-64107 | SKLPD0021-00 | 3107-XZV-64107 |  | 3107-Z-6456 | 3107-XZY-64107 | Отс. клап. на входе 3107-HOP-6406AB | 3107-HOP-6406AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR08 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3107-XZY-64107/3102-S-JB-D144 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 2 | [12 empty] | Запись в БД произведена
808 | 3102 | 3102 | 3107-XZV-64107 | SKLPD0021-00 | 3107-XZV-64107 |  |  | 3107-XZZSC-64107 | Отс. клап. на входе 3107-HOP-6406AB (закрыт) | 3107-HOP-6406AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C140/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C140 |  |  | 3107-XZZSC-64107/3102-S-JB-C140 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 16 | [12 empty] | Запись в БД произведена
809 | 3102 | 3102 | 3107-XZV-64107 | SKLPD0021-00 | 3107-XZV-64107 |  |  | 3107-XZZSO-64107 | Отс. клап. на входе 3107-HOP-6406AB (открыт) | 3107-HOP-6406AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSO-64107/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 31 | [12 empty] | Запись в БД произведена
811 | 3102 | 3102 | 3107-XZV-64108 | SKLPD0021-00 | 3107-XZV-64108 |  |  | 3107-XZV-64108 | Отс. клап. на выходе 3107-HOP-6406AB | 3107-HOP-6406AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
812 | 3102 | 3102 | 3107-XZV-64108 | SKLPD0021-00 | 3107-XZV-64108 |  | 3107-Z-6456 | 3107-XZY-64108 | Отс. клап. на выходе 3107-HOP-6406AB | 3107-HOP-6406AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR02 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64108/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 5 | [12 empty] | Запись в БД произведена
813 | 3102 | 3102 | 3107-XZV-64108 | SKLPD0021-00 | 3107-XZV-64108 |  |  | 3107-XZZSC-64108 | Отс. клап. на выходе 3107-HOP-6406AB (закрыт) | 3107-HOP-6406AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3107-XZZSC-64108/3102-S-JB-C141 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 18 | [12 empty] | Запись в БД произведена
814 | 3102 | 3102 | 3107-XZV-64108 | SKLPD0021-00 | 3107-XZV-64108 |  |  | 3107-XZZSO-64108 | Отс. клап. на выходе 3107-HOP-6406AB (открыт) | 3107-HOP-6406AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3107-XZZSO-64108/3102-S-JB-C141 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 23 | [12 empty] | Запись в БД произведена
816 | 2202 | 3102 | 3107-MXI-46405A | SDO0001-01 | 3107-MXI-46405A |  | 3107-Z-6412, 3107-Z-6455, 3102-Z-6290 | 3107-MXI-46405A | SIS стоп насоса HTF первого преполим. 3107-HOP-6405A | First Pre-Polymerizer HTF Pump 3107-HOP-6405A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6403 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 15 | [12 empty] | Запись в БД произведена
818 | 2202 | 3102 | 3107-MXI-56405A | SDO0001-01 | 3107-MXI-56405A |  | 3107-Z-6412, 3107-Z-6455, 3102-Z-6290 | 3107-MXI-56405A | SIS стоп насоса HTF первого преполим. 3107-HOP-6405B | First Pre-Polymerizer HTF Pump 3107-HOP-6405B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6403 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 7 | [12 empty] | Запись в БД произведена
820 | 2202 | 3102 | 3107-MXI-46406A | SDO0001-01 | 3107-MXI-46406A |  | 3107-Z-6413, 3107-Z-6456, 3102-Z-6290 | 3107-MXI-46406A | SIS стоп насоса HTF второго преполим. 3107-HOP-6406A | Second Pre-Polymerizer HTF Pump 3107-HOP-6406A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6403 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 16 | [12 empty] | Запись в БД произведена
822 | 2202 | 3102 | 3107-MXI-56406A | SDO0001-01 | 3107-MXI-56406A |  | 3107-Z-6413, 3107-Z-6456, 3102-Z-6290 | 3107-MXI-56406A | SIS стоп насоса HTF второго преполим. 3107-HOP-6406B | Second Pre-Polymerizer HTF Pump 3107-HOP-6406B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6403 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 8 | [12 empty] | Запись в БД произведена
824 | 3102 | 3102 | 3107-LZSA-64107A | SDI0010-01R | 3107-LZSA-64107A |  | 3107-Z-6414 | 3107-LZS-64107A | Ур. на входе 3107-HOP-6407A | 3107-HOP-6407A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C128/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 454 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C128 |  |  | 3107-LZS-64107A/3102-S-JB-C128 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 6 | [12 empty] | Запись в БД произведена
826 | 3102 | 3102 | 3107-LZSA-64107B | SDI0010-01R | 3107-LZSA-64107B |  | 3107-Z-6414 | 3107-LZS-64107B | Ур. на входе 3107-HOP-6407B | 3107-HOP-6407B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C129/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 448 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C129 |  |  | 3107-LZS-64107B/3102-S-JB-C129 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 11 | [12 empty] | Запись в БД произведена
828 | 3102 | 3102 | 3107-LZSA-64107C | SDI0010-01R | 3107-LZSA-64107C |  | 3107-Z-6414 | 3107-LZS-64107C | Ур. на входе 3107-HOP-6407C | 3107-HOP-6407C Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C130/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 494 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C130 |  |  | 3107-LZS-64107C/3102-S-JB-C130 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 9 | [12 empty] | Запись в БД произведена
830 | 3102 | 3102 | 3107-XZV-64109 | SKLPD0021-00 | 3107-XZV-64109 |  |  | 3107-XZV-64109 | Отс. клап. на входе 3107-HOP-6407AB | 3107-HOP-6407AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
831 | 3102 | 3102 | 3107-XZV-64109 | SKLPD0021-00 | 3107-XZV-64109 |  | 3107-Z-6457 | 3107-XZY-64109 | Отс. клап. на входе 3107-HOP-6407AB | 3107-HOP-6407AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR03 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64109/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 6 | [12 empty] | Запись в БД произведена
832 | 3102 | 3102 | 3107-XZV-64109 | SKLPD0021-00 | 3107-XZV-64109 |  |  | 3107-XZZSC-64109 | Отс. клап. на входе 3107-HOP-6407AB (закрыт) | 3107-HOP-6407AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3107-XZZSC-64109/3102-S-JB-C141 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 19 | [12 empty] | Запись в БД произведена
833 | 3102 | 3102 | 3107-XZV-64109 | SKLPD0021-00 | 3107-XZV-64109 |  |  | 3107-XZZSO-64109 | Отс. клап. на входе 3107-HOP-6407AB (открыт) | 3107-HOP-6407AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3107-XZZSO-64109/3102-S-JB-C141 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 24 | [12 empty] | Запись в БД произведена
835 | 3102 | 3102 | 3107-XZV-64110 | SKLPD0021-00 | 3107-XZV-64110 |  |  | 3107-XZV-64110 | Отс. клап. на выходе 3107-HOP-6407AB | 3107-HOP-6407AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
836 | 3102 | 3102 | 3107-XZV-64110 | SKLPD0021-00 | 3107-XZV-64110 |  | 3107-Z-6457 | 3107-XZY-64110 | Отс. клап. на выходе 3107-HOP-6407AB | 3107-HOP-6407AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR04 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64110/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 7 | [12 empty] | Запись в БД произведена
837 | 3102 | 3102 | 3107-XZV-64110 | SKLPD0021-00 | 3107-XZV-64110 |  |  | 3107-XZZSC-64110 | Отс. клап. на выходе 3107-HOP-6407AB (закрыт) | 3107-HOP-6407AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSC-64110/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 27 | [12 empty] | Запись в БД произведена
838 | 3102 | 3102 | 3107-XZV-64110 | SKLPD0021-00 | 3107-XZV-64110 |  |  | 3107-XZZSO-64110 | Отс. клап. на выходе 3107-HOP-6407AB (открыт) | 3107-HOP-6407AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSO-64110/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 0 | [12 empty] | Запись в БД произведена
840 | 3102 | 3102 | 3107-XZV-64111 | SKLPD0021-00 | 3107-XZV-64111 |  |  | 3107-XZV-64111 | Отс. клап. на входе 3107-HOP-6407C | 3107-HOP-6407C Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
841 | 3102 | 3102 | 3107-XZV-64111 | SKLPD0021-00 | 3107-XZV-64111 |  | 3107-Z-6467 | 3107-XZY-64111 | Отс. клап. на входе 3107-HOP-6407C | 3107-HOP-6407C Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR05 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64111/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 8 | [12 empty] | Запись в БД произведена
842 | 3102 | 3102 | 3107-XZV-64111 | SKLPD0021-00 | 3107-XZV-64111 |  |  | 3107-XZZSC-64111 | Отс. клап. на входе 3107-HOP-6407C (закрыт) | 3107-HOP-6407C Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3107-XZZSC-64111/3102-S-JB-C141 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 20 | [12 empty] | Запись в БД произведена
843 | 3102 | 3102 | 3107-XZV-64111 | SKLPD0021-00 | 3107-XZV-64111 |  |  | 3107-XZZSO-64111 | Отс. клап. на входе 3107-HOP-6407C (открыт) | 3107-HOP-6407C Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3107-XZZSO-64111/3102-S-JB-C141 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 25 | [12 empty] | Запись в БД произведена
845 | 3102 | 3102 | 3107-XZV-64112 | SKLPD0021-00 | 3107-XZV-64112 |  |  | 3107-XZV-64112 | Отс. клап. на выходе 3107-HOP-6407C | 3107-HOP-6407C Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
846 | 3102 | 3102 | 3107-XZV-64112 | SKLPD0021-00 | 3107-XZV-64112 |  | 3107-Z-6467 | 3107-XZY-64112 | Отс. клап. на выходе 3107-HOP-6407C | 3107-HOP-6407C Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR06 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64112/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 9 | [12 empty] | Запись в БД произведена
847 | 3102 | 3102 | 3107-XZV-64112 | SKLPD0021-00 | 3107-XZV-64112 |  |  | 3107-XZZSC-64112 | Отс. клап. на выходе 3107-HOP-6407C (закрыт) | 3107-HOP-6407C Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSC-64112/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 28 | [12 empty] | Запись в БД произведена
848 | 3102 | 3102 | 3107-XZV-64112 | SKLPD0021-00 | 3107-XZV-64112 |  |  | 3107-XZZSO-64112 | Отс. клап. на выходе 3107-HOP-6407C (открыт) | 3107-HOP-6407C Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSO-64112/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 1 | [12 empty] | Запись в БД произведена
850 | 2202 | 3102 | 3107-MXI-46407A | SDO0001-01 | 3107-MXI-46407A |  | 3107-Z-6414, 3107-Z-6457, 3102-Z-6290 | 3107-MXI-46407A | SIS стоп насоса HTF первого полимеризатора 3107-HOP-6407A | First Polymerizer HTF Pump 3107-HOP-6407A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6404 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 17 | [12 empty] | Запись в БД произведена
852 | 2202 | 3102 | 3107-MXI-56407A | SDO0001-01 | 3107-MXI-56407A |  | 3107-Z-6414, 3107-Z-6457, 3107-Z-6467, 3102-Z-6290 | 3107-MXI-56407A | SIS стоп насоса HTF первого полимеризатора 3107-HOP-6407B | First Polymerizer HTF Pump 3107-HOP-6407B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6404 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 9 | [12 empty] | Запись в БД произведена
854 | 2202 | 3102 | 3107-MXI-66407A | SDO0001-01 | 3107-MXI-66407A |  | 3107-Z-6414, 3107-Z-6467, 3102-Z-6290 | 3107-MXI-66407A | SIS стоп насоса HTF первого полимеризатора 3107-HOP-6407C | First Polymerizer HTF Pump 3107-HOP-6407C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6404 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 30 | [12 empty] | Запись в БД произведена
856 | 3102 | 3102 | 3107-LZSA-64108A | SDI0010-01R | 3107-LZSA-64108A |  | 3107-Z-6415 | 3107-LZS-64108A | Ур. на входе 3107-HOP-6408A | 3107-HOP-6408A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C128/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 454 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C128 |  |  | 3107-LZS-64108A/3102-S-JB-C128 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 7 | [12 empty] | Запись в БД произведена
858 | 3102 | 3102 | 3107-LZSA-64108B | SDI0010-01R | 3107-LZSA-64108B |  | 3107-Z-6415 | 3107-LZS-64108B | Ур. на входе 3107-HOP-6408B | 3107-HOP-6408B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C129/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 448 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C129 |  |  | 3107-LZS-64108B/3102-S-JB-C129 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 12 | [12 empty] | Запись в БД произведена
860 | 3102 | 3102 | 3107-LZSA-64108C | SDI0010-01R | 3107-LZSA-64108C |  | 3107-Z-6415 | 3107-LZS-64108C | Ур. на входе 3107-HOP-6408C | 3107-HOP-6408C Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C128/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 454 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C128 |  |  | 3107-LZS-64108C/3102-S-JB-C128 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 8 | [12 empty] | Запись в БД произведена
862 | 3102 | 3102 | 3107-XZV-64113 | SKLPD0021-00 | 3107-XZV-64113 |  |  | 3107-XZV-64113 | Отс. клап. на входе 3107-HOP-6408AB | 3107-HOP-6408AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
863 | 3102 | 3102 | 3107-XZV-64113 | SKLPD0021-00 | 3107-XZV-64113 |  | 3107-Z-6458 | 3107-XZY-64113 | Отс. клап. на входе 3107-HOP-6408AB | 3107-HOP-6408AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR07 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64113/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 10 | [12 empty] | Запись в БД произведена
864 | 3102 | 3102 | 3107-XZV-64113 | SKLPD0021-00 | 3107-XZV-64113 |  |  | 3107-XZZSC-64113 | Отс. клап. на входе 3107-HOP-6408AB (закрыт) | 3107-HOP-6408AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C141/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C141 |  |  | 3107-XZZSC-64113/3102-S-JB-C141 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 21 | [12 empty] | Запись в БД произведена
865 | 3102 | 3102 | 3107-XZV-64113 | SKLPD0021-00 | 3107-XZV-64113 |  |  | 3107-XZZSO-64113 | Отс. клап. на входе 3107-HOP-6408AB (открыт) | 3107-HOP-6408AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSO-64113/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 2 | [12 empty] | Запись в БД произведена
867 | 3102 | 3102 | 3107-XZV-64114 | SKLPD0021-00 | 3107-XZV-64114 |  |  | 3107-XZV-64114 | Отс. клап. на выходе 3107-HOP-6408AB | 3107-HOP-6408AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
868 | 3102 | 3102 | 3107-XZV-64114 | SKLPD0021-00 | 3107-XZV-64114 |  | 3107-Z-6458 | 3107-XZY-64114 | Отс. клап. на выходе 3107-HOP-6408AB | 3107-HOP-6408AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR08 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64114/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 11 | [12 empty] | Запись в БД произведена
869 | 3102 | 3102 | 3107-XZV-64114 | SKLPD0021-00 | 3107-XZV-64114 |  |  | 3107-XZZSC-64114 | Отс. клап. на выходе 3107-HOP-6408AB (закрыт) | 3107-HOP-6408AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSC-64114/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 6 | [12 empty] | Запись в БД произведена
870 | 3102 | 3102 | 3107-XZV-64114 | SKLPD0021-00 | 3107-XZV-64114 |  |  | 3107-XZZSO-64114 | Отс. клап. на выходе 3107-HOP-6408AB (открыт) | 3107-HOP-6408AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSO-64114/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 11 | [12 empty] | Запись в БД произведена
872 | 3102 | 3102 | 3107-XZV-64115 | SKLPD0021-00 | 3107-XZV-64115 |  |  | 3107-XZV-64115 | Отс. клап. на входе 3107-HOP-6408C | 3107-HOP-6408C Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
873 | 3102 | 3102 | 3107-XZV-64115 | SKLPD0021-00 | 3107-XZV-64115 |  | 3107-Z-6468 | 3107-XZY-64115 | Отс. клап. на входе 3107-HOP-6408C | 3107-HOP-6408C Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR09 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64115/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 12 | [12 empty] | Запись в БД произведена
874 | 3102 | 3102 | 3107-XZV-64115 | SKLPD0021-00 | 3107-XZV-64115 |  |  | 3107-XZZSC-64115 | Отс. клап. на входе 3107-HOP-6408C (закрыт) | 3107-HOP-6408C Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSC-64115/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 7 | [12 empty] | Запись в БД произведена
875 | 3102 | 3102 | 3107-XZV-64115 | SKLPD0021-00 | 3107-XZV-64115 |  |  | 3107-XZZSO-64115 | Отс. клап. на входе 3107-HOP-6408C (открыт) | 3107-HOP-6408C Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSO-64115/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 12 | [12 empty] | Запись в БД произведена
877 | 3102 | 3102 | 3107-XZV-64116 | SKLPD0021-00 | 3107-XZV-64116 |  |  | 3107-XZV-64116 | Отс. клап. на выходе 3107-HOP-6408C | 3107-HOP-6408C Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
878 | 3102 | 3102 | 3107-XZV-64116 | SKLPD0021-00 | 3107-XZV-64116 |  | 3107-Z-6468 | 3107-XZY-64116 | Отс. клап. на выходе 3107-HOP-6408C | 3107-HOP-6408C Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR10 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64116/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 13 | [12 empty] | Запись в БД произведена
879 | 3102 | 3102 | 3107-XZV-64116 | SKLPD0021-00 | 3107-XZV-64116 |  |  | 3107-XZZSC-64116 | Отс. клап. на выходе 3107-HOP-6408C (закрыт) | 3107-HOP-6408C Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSC-64116/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 8 | [12 empty] | Запись в БД произведена
880 | 3102 | 3102 | 3107-XZV-64116 | SKLPD0021-00 | 3107-XZV-64116 |  |  | 3107-XZZSO-64116 | Отс. клап. на выходе 3107-HOP-6408C (открыт) | 3107-HOP-6408C Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSO-64116/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 13 | [12 empty] | Запись в БД произведена
882 | 2202 | 3102 | 3107-MXI-46408A | SDO0001-01 | 3107-MXI-46408A |  | 3107-Z-6415, 3107-Z-6458, 3102-Z-6290 | 3107-MXI-46408A | SIS стоп насоса HTF второго полимеризатора 3107-HOP-6408A | Second Polymerizer HTF Pump 3107-HOP-6408A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6405 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 18 | [12 empty] | Запись в БД произведена
884 | 2202 | 3102 | 3107-MXI-56408A | SDO0001-01 | 3107-MXI-56408A |  | 3107-Z-6415, 3107-Z-6458, Z-6468, 3102-Z-6290 | 3107-MXI-56408A | SIS стоп насоса HTF второго полимеризатора 3107-HOP-6408B | Second Polymerizer HTF Pump 3107-HOP-6408B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6405 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 10 | [12 empty] | Запись в БД произведена
886 | 2202 | 3102 | 3107-MXI-66408A | SDO0001-01 | 3107-MXI-66408A |  | 3107-Z-6415, Z-6468, 3102-Z-6290 | 3107-MXI-66408A | SIS стоп насоса HTF второго полимеризатора 3107-HOP-6408C | Second Polymerizer HTF Pump 3107-HOP-6408C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6405 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 31 | [12 empty] | Запись в БД произведена
888 | 3102 | 3102 | 3107-LZSA-64109 | SDI0010-01R | 3107-LZSA-64109 |  | 3107-Z-6416 | 3107-LZS-64109 | Ур. на входе 3107-HOP-6409 | 3107-HOP-6409 Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C129/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 448 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C129 |  |  | 3107-LZS-64109/3102-S-JB-C129 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 13 | [12 empty] | Запись в БД произведена
890 | 3102 | 3102 | 3107-LZSA-64110A | SDI0010-01R | 3107-LZSA-64110A |  | 3107-Z-6417 | 3107-LZS-64110A | Ур. на входе 3107-HOP-6410A | 3107-HOP-6410A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C130/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 494 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C130 |  |  | 3107-LZS-64110A/3102-S-JB-C130 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 10 | [12 empty] | Запись в БД произведена
892 | 3102 | 3102 | 3107-LZSA-64110B | SDI0010-01R | 3107-LZSA-64110B |  | 3107-Z-6417 | 3107-LZS-64110B | Ур. на входе 3107-HOP-6410B | 3107-HOP-6410B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C130/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 494 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C130 |  |  | 3107-LZS-64110B/3102-S-JB-C130 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 11 | [12 empty] | Запись в БД произведена
894 | 3102 | 3102 | 3107-XZV-64117 | SKLPD0021-00 | 3107-XZV-64117 |  |  | 3107-XZV-64117 | Отс. клап. на входе 3107-HOP-6409 | 3107-HOP-6409 Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
895 | 3102 | 3102 | 3107-XZV-64117 | SKLPD0021-00 | 3107-XZV-64117 |  | 3107-Z-6459 | 3107-XZY-64117 | Отс. клап. на входе 3107-HOP-6409 | 3107-HOP-6409 Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR11 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64117/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 14 | [12 empty] | Запись в БД произведена
896 | 3102 | 3102 | 3107-XZV-64117 | SKLPD0021-00 | 3107-XZV-64117 |  |  | 3107-XZZSC-64117 | Отс. клап. на входе 3107-HOP-6409 (закрыт) | 3107-HOP-6409 Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSC-64117/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 9 | [12 empty] | Запись в БД произведена
897 | 3102 | 3102 | 3107-XZV-64117 | SKLPD0021-00 | 3107-XZV-64117 |  |  | 3107-XZZSO-64117 | Отс. клап. на входе 3107-HOP-6409 (открыт) | 3107-HOP-6409 Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSO-64117/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 14 | [12 empty] | Запись в БД произведена
899 | 3102 | 3102 | 3107-XZV-64118 | SKLPD0021-00 | 3107-XZV-64118 |  |  | 3107-XZV-64118 | Отс. клап. на выходе 3107-HOP-6409 | 3107-HOP-6409 Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
900 | 3102 | 3102 | 3107-XZV-64118 | SKLPD0021-00 | 3107-XZV-64118 |  | 3107-Z-6459 | 3107-XZY-64118 | Отс. клап. на выходе 3107-HOP-6409 | 3107-HOP-6409 Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D145/3000-S-MC-B12 | PR12 | NH-KYJYP3 37x2.5 | 511 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D145 |  |  | 3107-XZY-64118/3102-S-JB-D145 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 15 | [12 empty] | Запись в БД произведена
901 | 3102 | 3102 | 3107-XZV-64118 | SKLPD0021-00 | 3107-XZV-64118 |  |  | 3107-XZZSC-64118 | Отс. клап. на выходе 3107-HOP-6409 (закрыт) | 3107-HOP-6409 Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSC-64118/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 29 | [12 empty] | Запись в БД произведена
902 | 3102 | 3102 | 3107-XZV-64118 | SKLPD0021-00 | 3107-XZV-64118 |  |  | 3107-XZZSO-64118 | Отс. клап. на выходе 3107-HOP-6409 (открыт) | 3107-HOP-6409 Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSO-64118/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 3 | [12 empty] | Запись в БД произведена
904 | 3102 | 3102 | 3107-XZV-64119 | SKLPD0021-00 | 3107-XZV-64119 |  |  | 3107-XZV-64119 | Отс. клап. на входе 3107-HOP-6410AB | 3107-HOP-6410AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
905 | 3102 | 3102 | 3107-XZV-64119 | SKLPD0021-00 | 3107-XZV-64119 |  | 3107-Z-6460 | 3107-XZY-64119 | Отс. клап. на входе 3107-HOP-6410AB | 3107-HOP-6410AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR09 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3107-XZY-64119/3102-S-JB-D144 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 3 | [12 empty] | Запись в БД произведена
906 | 3102 | 3102 | 3107-XZV-64119 | SKLPD0021-00 | 3107-XZV-64119 |  |  | 3107-XZZSC-64119 | Отс. клап. на входе 3107-HOP-6410AB (закрыт) | 3107-HOP-6410AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSC-64119/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 10 | [12 empty] | Запись в БД произведена
907 | 3102 | 3102 | 3107-XZV-64119 | SKLPD0021-00 | 3107-XZV-64119 |  |  | 3107-XZZSO-64119 | Отс. клап. на входе 3107-HOP-6410AB (открыт) | 3107-HOP-6410AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C143/3000-S-MC-B06 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 509 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C143 |  |  | 3107-XZZSO-64119/3102-S-JB-C143 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 15 | [12 empty] | Запись в БД произведена
909 | 3102 | 3102 | 3107-XZV-64120 | SKLPD0021-00 | 3107-XZV-64120 |  |  | 3107-XZV-64120 | Отс. клап. на выходе 3107-HOP-6410AB | 3107-HOP-6410AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
910 | 3102 | 3102 | 3107-XZV-64120 | SKLPD0021-00 | 3107-XZV-64120 |  | 3107-Z-6460 | 3107-XZY-64120 | Отс. клап. на выходе 3107-HOP-6410AB | 3107-HOP-6410AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D144/3000-S-MC-B12 | PR10 | NH-KYJYP3 24x2.5 | 509 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D144 |  |  | 3107-XZY-64120/3102-S-JB-D144 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 4 | [12 empty] | Запись в БД произведена
911 | 3102 | 3102 | 3107-XZV-64120 | SKLPD0021-00 | 3107-XZV-64120 |  |  | 3107-XZZSC-64120 | Отс. клап. на выходе 3107-HOP-6410AB (закрыт) | 3107-HOP-6410AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSC-64120/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 08 | - | A21-08 | - | A22-08 | - | 30 | [12 empty] | Запись в БД произведена
912 | 3102 | 3102 | 3107-XZV-64120 | SKLPD0021-00 | 3107-XZV-64120 |  |  | 3107-XZZSO-64120 | Отс. клап. на выходе 3107-HOP-6410AB (открыт) | 3107-HOP-6410AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C142/3000-S-MC-B06 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 499 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C142 |  |  | 3107-XZZSO-64120/3102-S-JB-C142 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 4 | [12 empty] | Запись в БД произведена
914 | 2202 | 3102 | 3107-MXI-46409A | SDO0001-01 | 3107-MXI-46409A |  | 3107-Z-6416, 3107-Z-6459, 3102-Z-6290 | 3107-MXI-46409A | SIS стоп верхнего насоса HTF третьего полимеризатора 3107-HOP-6409 | Third Polymerizer Upper HTF Pump 3107-HOP-6409 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6406 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 19 | [12 empty] | Запись в БД произведена
916 | 2202 | 3102 | 3107-MXI-46410A | SDO0001-01 | 3107-MXI-46410A |  | 3107-Z-6417, 3107-Z-6460, 3102-Z-6290 | 3107-MXI-46410A | SIS стоп нижнего насоса HTF третьего полимеризатора 3107-HOP-6410A | Third Polymerizer Lower HTF Pump 3107-HOP-6410A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6406 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 20 | [12 empty] | Запись в БД произведена
918 | 2202 | 3102 | 3107-MXI-56410A | SDO0001-01 | 3107-MXI-56410A |  | 3107-Z-6417, 3107-Z-6459, 3107-Z-6460, 3102-Z-6290 | 3107-MXI-56410A | SIS стоп нижнего насоса HTF третьего полимеризатора 3107-HOP-6410B | Third Polymerizer Lower HTF Pump 3107-HOP-6410B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6406 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 11 | [12 empty] | Запись в БД произведена
920 | 3103 | 3103 | 3107-LZSA-64011A | SDI0010-01R | 3107-LZSA-64011A |  | 3107-Z-6418 | 3107-LZS-64011A | Ур. на входе 3107-HOP-6411A | 3107-HOP-6411A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C198/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C198 |  |  | 3107-LZS-64011A/3103-S-JB-C198 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 13 | [12 empty] | Запись в БД произведена
922 | 3103 | 3103 | 3107-LZSA-64011B | SDI0010-01R | 3107-LZSA-64011B |  | 3107-Z-6418 | 3107-LZS-64011B | Ур. на входе 3107-HOP-6411B | 3107-HOP-6411B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C203/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C203 |  |  | 3107-LZS-64011B/3103-S-JB-C203 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 18 | [12 empty] | Запись в БД произведена
924 | 3101 | 3101 | 3107-LZSA-64101 | SDI0010-01R | 3107-LZSA-64101 |  | 3107-Z-6450 | 3107-LZS-64101 | Ур. на входе 3107-HOP-6001 | 3107-HOP-6001 Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C105/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C105 |  |  | 3107-LZS-64101/3101-S-JB-C105 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 6 | [12 empty] | Запись в БД произведена
926 | 3101 | 3101 | 3107-XZV-64020 | SKLPD0021-00 | 3107-XZV-64020 |  |  | 3107-XZV-64020 | Отс. клап. на входе 3107-HOP-6001 | 3107-HOP-6001 Inlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6407 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
927 | 3101 | 3101 | 3107-XZV-64020 | SKLPD0021-00 | 3107-XZV-64020 |  | 3107-Z-6470 | 3107-XZY-64020 | Отс. клап. на входе 3107-HOP-6001 | 3107-HOP-6001 Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6407 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D106/3000-S-MC-B13 | PR06 | NH-KYJYP3 24x2.5 | 383 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D106 |  |  | 3107-XZY-64020/3101-S-JB-D106 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 5 | [12 empty] | Запись в БД произведена
928 | 3101 | 3101 | 3107-XZV-64020 | SKLPD0021-00 | 3107-XZV-64020 |  |  | 3107-XZZSC-64020 | Отс. клап. на входе 3107-HOP-6001 (закрыт) | 3107-HOP-6001 Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C104/3000-S-MC-B08 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C104 |  |  | 3107-XZZSC-64020/3101-S-JB-C104 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 4 | [12 empty] | Запись в БД произведена
929 | 3101 | 3101 | 3107-XZV-64020 | SKLPD0021-00 | 3107-XZV-64020 |  |  | 3107-XZZSO-64020 | Отс. клап. на входе 3107-HOP-6001 (открыт) | 3107-HOP-6001 Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C104/3000-S-MC-B08 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C104 |  |  | 3107-XZZSO-64020/3101-S-JB-C104 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 6 | [12 empty] | Запись в БД произведена
931 | 3101 | 3101 | 3107-XZV-64021 | SKLPD0021-00 | 3107-XZV-64021 |  |  | 3107-XZV-64021 | Отс. клап. на выходе 3107-HOP-6001 | 3107-HOP-6001 outlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6407 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
932 | 3101 | 3101 | 3107-XZV-64021 | SKLPD0021-00 | 3107-XZV-64021 |  | 3107-Z-6470 | 3107-XZY-64021 | Отс. клап. на выходе 3107-HOP-6001 | 3107-HOP-6001 outlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6407 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-D106/3000-S-MC-B13 | PR07 | NH-KYJYP3 24x2.5 | 383 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3101-S-JB-D106 |  |  | 3107-XZY-64021/3101-S-JB-D106 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 6 | [12 empty] | Запись в БД произведена
933 | 3101 | 3101 | 3107-XZV-64021 | SKLPD0021-00 | 3107-XZV-64021 |  |  | 3107-XZZSC-64021 | Отс. клап. на выходе 3107-HOP-6001 (закрыт) | 3107-HOP-6001 outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C104/3000-S-MC-B08 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C104 |  |  | 3107-XZZSC-64021/3101-S-JB-C104 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 5 | [12 empty] | Запись в БД произведена
934 | 3101 | 3101 | 3107-XZV-64021 | SKLPD0021-00 | 3107-XZV-64021 |  |  | 3107-XZZSO-64021 | Отс. клап. на выходе 3107-HOP-6001 (открыт) | 3107-HOP-6001 outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C104/3000-S-MC-B08 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C104 |  |  | 3107-XZZSO-64021/3101-S-JB-C104 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 7 | [12 empty] | Запись в БД произведена
936 | 3103 | 3103 | 3107-XZV-64121 | SKLPD0021-00 | 3107-XZV-64121 |  |  | 3107-XZV-64121 | Отс. клап. на входе 3107-HOP-6411AB | 3107-HOP-6411AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
937 | 3103 | 3103 | 3107-XZV-64121 | SKLPD0021-00 | 3107-XZV-64121 |  | 3107-Z-6461 | 3107-XZY-64121 | Отс. клап. на входе 3107-HOP-6411AB | 3107-HOP-6411AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR02 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64121/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 2 | [12 empty] | Запись в БД произведена
938 | 3103 | 3103 | 3107-XZV-64121 | SKLPD0021-00 | 3107-XZV-64121 |  |  | 3107-XZZSC-64121 | Отс. клап. на входе 3107-HOP-6411AB (закрыт) | 3107-HOP-6411AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3107-XZZSC-64121/3103-S-JB-C211 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 5 | [12 empty] | Запись в БД произведена
939 | 3103 | 3103 | 3107-XZV-64121 | SKLPD0021-00 | 3107-XZV-64121 |  |  | 3107-XZZSO-64121 | Отс. клап. на входе 3107-HOP-6411AB (открыт) | 3107-HOP-6411AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3107-XZZSO-64121/3103-S-JB-C211 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 7 | [12 empty] | Запись в БД произведена
941 | 3103 | 3103 | 3107-XZV-64122 | SKLPD0021-00 | 3107-XZV-64122 |  |  | 3107-XZV-64122 | Отс. клап. на выходе 3107-HOP-6411AB | 3107-HOP-6411AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
942 | 3103 | 3103 | 3107-XZV-64122 | SKLPD0021-00 | 3107-XZV-64122 |  | 3107-Z-6461 | 3107-XZY-64122 | Отс. клап. на выходе 3107-HOP-6411AB | 3107-HOP-6411AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR03 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64122/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 3 | [12 empty] | Запись в БД произведена
943 | 3103 | 3103 | 3107-XZV-64122 | SKLPD0021-00 | 3107-XZV-64122 |  |  | 3107-XZZSC-64122 | Отс. клап. на выходе 3107-HOP-6411AB (закрыт) | 3107-HOP-6411AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3107-XZZSC-64122/3103-S-JB-C211 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 6 | [12 empty] | Запись в БД произведена
944 | 3103 | 3103 | 3107-XZV-64122 | SKLPD0021-00 | 3107-XZV-64122 |  |  | 3107-XZZSO-64122 | Отс. клап. на выходе 3107-HOP-6411AB (открыт) | 3107-HOP-6411AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3107-XZZSO-64122/3103-S-JB-C211 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 8 | [12 empty] | Запись в БД произведена
946 | 2202 | 3101 | 3107-MXI-46001A | SDO0001-01 | 3107-MXI-46001A |  | 3101-Z-6001, 3101-Z-6003, 3101-Z-6004, 3101-Z-6006, 3101-Z-6007, 3107-Z-6450, 3107-Z-6470, 3101-Z-6090 | 3107-MXI-46001A | SIS стоп насоса HTF нагревателя растворения 3107-HOP-6001 | Dissolution Heater HTF Pump 3107-HOP-6001 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6407 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 10 | [12 empty] | Запись в БД произведена
948 | 2202 | 3103 | 3107-MXI-46411A | SDO0001-01 | 3107-MXI-46411A |  | 3107-Z-6418, 3107-Z-6461, 3103-Z-6292 | 3107-MXI-46411A | SIS стоп насоса HTF подогревателя дегазации 3107-HOP-6411A | Devolatilization Heater HTF Pump 3107-HOP-6411A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6407 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 21 | [12 empty] | Запись в БД произведена
950 | 2202 | 3103 | 3107-MXI-56411A | SDO0001-01 | 3107-MXI-56411A |  | 3107-Z-6418, 3107-Z-6461, 3103-Z-6292 | 3107-MXI-56411A | SIS стоп насоса HTF подогревателя дегазации 3107-HOP-6411B | Devolatilization Heater HTF Pump 3107-HOP-6411B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6407 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 12 | [12 empty] | Запись в БД произведена
952 | 3103 | 3103 | 3107-LZSA-64012A | SDI0010-01R | 3107-LZSA-64012A |  | 3107-Z-6419 | 3107-LZS-64012A | Ур. на входе 3107-HOP-6412A | 3107-HOP-6412A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C198/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C198 |  |  | 3107-LZS-64012A/3103-S-JB-C198 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 14 | [12 empty] | Запись в БД произведена
954 | 3103 | 3103 | 3107-LZSA-64012B | SDI0010-01R | 3107-LZSA-64012B |  | 3107-Z-6419 | 3107-LZS-64012B | Ур. на входе 3107-HOP-6412B | 3107-HOP-6412B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C203/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C203 |  |  | 3107-LZS-64012B/3103-S-JB-C203 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 19 | [12 empty] | Запись в БД произведена
956 | 3103 | 3103 | 3107-LZSA-64013A | SDI0010-01R | 3107-LZSA-64013A |  | 3107-Z-6420 | 3107-LZS-64013A | Ур. на входе 3107-HOP-6413A | 3107-HOP-6413A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C198/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C198 |  |  | 3107-LZS-64013A/3103-S-JB-C198 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 15 | [12 empty] | Запись в БД произведена
958 | 3103 | 3103 | 3107-LZSA-64013B | SDI0010-01R | 3107-LZSA-64013B |  | 3107-Z-6420 | 3107-LZS-64013B | Ур. на входе 3107-HOP-6413B | 3107-HOP-6413B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C203/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C203 |  |  | 3107-LZS-64013B/3103-S-JB-C203 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 20 | [12 empty] | Запись в БД произведена
960 | 3103 | 3103 | 3107-XZV-64123 | SKLPD0021-00 | 3107-XZV-64123 |  |  | 3107-XZV-64123 | Отс. клап. на входе 3107-HOP-6412AB | 3107-HOP-6412AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
961 | 3103 | 3103 | 3107-XZV-64123 | SKLPD0021-00 | 3107-XZV-64123 |  | 3107-Z-6462 | 3107-XZY-64123 | Отс. клап. на входе 3107-HOP-6412AB | 3107-HOP-6412AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR04 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64123/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 4 | [12 empty] | Запись в БД произведена
962 | 3103 | 3103 | 3107-XZV-64123 | SKLPD0021-00 | 3107-XZV-64123 |  |  | 3107-XZZSC-64123 | Отс. клап. на входе 3107-HOP-6412AB (закрыт) | 3107-HOP-6412AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3107-XZZSC-64123/3103-S-JB-C210 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 16 | [12 empty] | Запись в БД произведена
963 | 3103 | 3103 | 3107-XZV-64123 | SKLPD0021-00 | 3107-XZV-64123 |  |  | 3107-XZZSO-64123 | Отс. клап. на входе 3107-HOP-6412AB (открыт) | 3107-HOP-6412AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3107-XZZSO-64123/3103-S-JB-C210 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 20 | [12 empty] | Запись в БД произведена
965 | 3103 | 3103 | 3107-XZV-64124 | SKLPD0021-00 | 3107-XZV-64124 |  |  | 3107-XZV-64124 | Отс. клап. на выходе 3107-HOP-6412AB | 3107-HOP-6412AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
966 | 3103 | 3103 | 3107-XZV-64124 | SKLPD0021-00 | 3107-XZV-64124 |  | 3107-Z-6462 | 3107-XZY-64124 | Отс. клап. на выходе 3107-HOP-6412AB | 3107-HOP-6412AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR05 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64124/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 5 | [12 empty] | Запись в БД произведена
967 | 3103 | 3103 | 3107-XZV-64124 | SKLPD0021-00 | 3107-XZV-64124 |  |  | 3107-XZZSC-64124 | Отс. клап. на выходе 3107-HOP-6412AB (закрыт) | 3107-HOP-6412AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3107-XZZSC-64124/3103-S-JB-C210 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 17 | [12 empty] | Запись в БД произведена
968 | 3103 | 3103 | 3107-XZV-64124 | SKLPD0021-00 | 3107-XZV-64124 |  |  | 3107-XZZSO-64124 | Отс. клап. на выходе 3107-HOP-6412AB (открыт) | 3107-HOP-6412AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3107-XZZSO-64124/3103-S-JB-C210 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 21 | [12 empty] | Запись в БД произведена
970 | 3103 | 3103 | 3107-XZV-64125 | SKLPD0021-00 | 3107-XZV-64125 |  |  | 3107-XZV-64125 | Отс. клап. на входе 3107-HOP-6413AB | 3107-HOP-6413AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
971 | 3103 | 3103 | 3107-XZV-64125 | SKLPD0021-00 | 3107-XZV-64125 |  | 3107-Z-6463 | 3107-XZY-64125 | Отс. клап. на входе 3107-HOP-6413AB | 3107-HOP-6413AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR06 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64125/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 6 | [12 empty] | Запись в БД произведена
972 | 3103 | 3103 | 3107-XZV-64125 | SKLPD0021-00 | 3107-XZV-64125 |  |  | 3107-XZZSC-64125 | Отс. клап. на входе 3107-HOP-6413AB (закрыт) | 3107-HOP-6413AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3107-XZZSC-64125/3103-S-JB-C210 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 18 | [12 empty] | Запись в БД произведена
973 | 3103 | 3103 | 3107-XZV-64125 | SKLPD0021-00 | 3107-XZV-64125 |  |  | 3107-XZZSO-64125 | Отс. клап. на входе 3107-HOP-6413AB (открыт) | 3107-HOP-6413AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3107-XZZSO-64125/3103-S-JB-C210 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 22 | [12 empty] | Запись в БД произведена
975 | 3103 | 3103 | 3107-XZV-64126 | SKLPD0021-00 | 3107-XZV-64126 |  |  | 3107-XZV-64126 | Отс. клап. на выходе 3107-HOP-6413AB | 3107-HOP-6413AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
976 | 3103 | 3103 | 3107-XZV-64126 | SKLPD0021-00 | 3107-XZV-64126 |  | 3107-Z-6463 | 3107-XZY-64126 | Отс. клап. на выходе 3107-HOP-6413AB | 3107-HOP-6413AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR07 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64126/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 7 | [12 empty] | Запись в БД произведена
977 | 3103 | 3103 | 3107-XZV-64126 | SKLPD0021-00 | 3107-XZV-64126 |  |  | 3107-XZZSC-64126 | Отс. клап. на выходе 3107-HOP-6413AB (закрыт) | 3107-HOP-6413AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3107-XZZSC-64126/3103-S-JB-C210 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 19 | [12 empty] | Запись в БД произведена
978 | 3103 | 3103 | 3107-XZV-64126 | SKLPD0021-00 | 3107-XZV-64126 |  |  | 3107-XZZSO-64126 | Отс. клап. на выходе 3107-HOP-6413AB (открыт) | 3107-HOP-6413AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C210/3000-S-MC-B06 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 484 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C210 |  |  | 3107-XZZSO-64126/3103-S-JB-C210 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 09 | - | A21-09 | - | A22-09 | - | 23 | [12 empty] | Запись в БД произведена
980 | 2202 | 3103 | 3107-MXI-46412A | SDO0001-01 | 3107-MXI-46412A |  | 3107-Z-6419, 3107-Z-6462, 3103-Z-6292 | 3107-MXI-46412A | SIS стоп насоса HTF системы основной дегазации 3107-HOP-6412A | Main Devolatilization Sytem HTF Pump 3107-HOP-6412A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6408 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 22 | [12 empty] | Запись в БД произведена
982 | 2202 | 3103 | 3107-MXI-56412A | SDO0001-01 | 3107-MXI-56412A |  | 3107-Z-6419, 3107-Z-6462, 3103-Z-6292 | 3107-MXI-56412A | SIS стоп насоса HTF системы основной дегазации 3107-HOP-6412B | Main Devolatilization Sytem HTF Pump 3107-HOP-6412B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6408 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 13 | [12 empty] | Запись в БД произведена
984 | 2202 | 3103 | 3107-MXI-46413A | SDO0001-01 | 3107-MXI-46413A |  | 3107-Z-6420, 3107-Z-6463, 3103-Z-6292 | 3107-MXI-46413A | SIS стоп насоса HTF системы финальной дегазации 3107-HOP-6413A | Final Devolatilization System HTF PUMP 3107-HOP-6413A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6408 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 23 | [12 empty] | Запись в БД произведена
986 | 2202 | 3103 | 3107-MXI-56413A | SDO0001-01 | 3107-MXI-56413A |  | 3107-Z-6420, 3107-Z-6463, 3103-Z-6292 | 3107-MXI-56413A | SIS стоп насоса HTF системы финальной дегазации 3107-HOP-6413B | Final Devolatilization System HTF PUMP 3107-HOP-6413B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6408 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 14 | [12 empty] | Запись в БД произведена
988 | 3103 | 3103 | 3107-LZIA-64002 | SAI1000-01R | 3107-LZIA-64002 |  | 3107-Z-6421 | 3107-LZT-64002 | Уровень в 3107-V-6401, сигн. H, L | 3107-V-6401 Liquid level indication HL alarm | D/P Level Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6409 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2000 | mm | 0 | 100 | % | 15 | 20 | 80 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3107-LZT-64002/3000-S-MC-B03 |  | NH-IA-DJYYP3 1x2x1.5 | 455 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B03 | Одиночный |  | 3107-LZT-64002/3000-S-MC-B03 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 03 | - | A21-03 | - | A22-03 | - | 3 | [12 empty] | Запись в БД произведена
990 | 3103 | 3103 | 3107-XZV-64140 | SKLPD0021-00 | 3107-XZV-64140 |  |  | 3107-XZV-64140 | Отс. клап. на входе 3107-HOP-6401ABC | 3107-HOP-6401ABC Inlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
991 | 3103 | 3103 | 3107-XZV-64140 | SKLPD0021-00 | 3107-XZV-64140 |  | 3107-Z-6451 | 3107-XZY-64140 | Отс. клап. на входе 3107-HOP-6401ABC | 3107-HOP-6401ABC Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR12 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64140/3103-S-JB-D213 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 18 | [12 empty] | Запись в БД произведена
992 | 3103 | 3103 | 3107-XZV-64140 | SKLPD0021-00 | 3107-XZV-64140 |  |  | 3107-XZZSC-64140 | Отс. клап. на входе 3107-HOP-6401ABC (закрыт) | 3107-HOP-6401ABC Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3107-XZZSC-64140/3103-S-JB-C211 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 18 | [12 empty] | Запись в БД произведена
993 | 3103 | 3103 | 3107-XZV-64140 | SKLPD0021-00 | 3107-XZV-64140 |  |  | 3107-XZZSO-64140 | Отс. клап. на входе 3107-HOP-6401ABC (открыт) | 3107-HOP-6401ABC Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C211/3000-S-MC-B06 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 476 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C211 |  |  | 3107-XZZSO-64140/3103-S-JB-C211 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 19 | [12 empty] | Запись в БД произведена
995 | 3102 | 3102 | 3107-XZV-64141 | SKLPD0021-00 | 3107-XZV-64141 |  |  | 3107-XZV-64141 | Отс. клап. на выходе 3107-HOP-6401AB | 3107-HOP-6401AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
996 | 3102 | 3102 | 3107-XZV-64141 | SKLPD0021-00 | 3107-XZV-64141 |  | 3107-Z-6466, 3107-Z-6451, 3107-Z-6499 | 3107-XZY-64141 | Отс. клап. на выходе 3107-HOP-6401AB | 3107-HOP-6401AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D157/3000-S-MC-B12 | PR07 | NH-KYJYP3 24x2.5 | 427 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D157 |  |  | 3107-XZY-64141/3102-S-JB-D157 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 16 | [12 empty] | Запись в БД произведена
997 | 3102 | 3102 | 3107-XZV-64141 | SKLPD0021-00 | 3107-XZV-64141 |  |  | 3107-XZZSC-64141 | Отс. клап. на выходе 3107-HOP-6401AB (закрыт) | 3107-HOP-6401AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSC-64141/3102-S-JB-C154 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 16 | [12 empty] | Запись в БД произведена
998 | 3102 | 3102 | 3107-XZV-64141 | SKLPD0021-00 | 3107-XZV-64141 |  |  | 3107-XZZSO-64141 | Отс. клап. на выходе 3107-HOP-6401AB (открыт) | 3107-HOP-6401AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C154/3000-S-MC-B06 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 446 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C154 |  |  | 3107-XZZSO-64141/3102-S-JB-C154 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 17 | [12 empty] | Запись в БД произведена
1000 | 3102 | 3102 | 3107-XZV-64142 | SKLPD0021-00 | 3107-XZV-64142 |  |  | 3107-XZV-64142 | Отс. клап. на выходе 3107-HOP-6401BC | 3107-HOP-6401BC Outlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1001 | 3102 | 3102 | 3107-XZV-64142 | SKLPD0021-00 | 3107-XZV-64142 |  | 3107-Z-6451, 3107-Z-7466, 3107-Z-6499 | 3107-XZY-64142 | Отс. клап. на выходе 3107-HOP-6401BC | 3107-HOP-6401BC Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-D158/3000-S-MC-B12 | PR04 | NH-KYJYP3 16x2.5 | 473 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3102-S-JB-D158 |  |  | 3107-XZY-64142/3102-S-JB-D158 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 17 | [12 empty] | Запись в БД произведена
1002 | 3102 | 3102 | 3107-XZV-64142 | SKLPD0021-00 | 3107-XZV-64142 |  |  | 3107-XZZSC-64142 | Отс. клап. на выходе 3107-HOP-6401BC (закрыт) | 3107-HOP-6401BC Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C156/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 446 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C156 |  |  | 3107-XZZSC-64142/3102-S-JB-C156 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 16 | [12 empty] | Запись в БД произведена
1003 | 3102 | 3102 | 3107-XZV-64142 | SKLPD0021-00 | 3107-XZV-64142 |  |  | 3107-XZZSO-64142 | Отс. клап. на выходе 3107-HOP-6401BC (открыт) | 3107-HOP-6401BC Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 (SCS2->SCS3) | 2490157-3000-PR007-6409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3102-S-JB-C156/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 446 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3102-S-JB-C156 |  |  | 3107-XZZSO-64142/3102-S-JB-C156 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 17 | [12 empty] | Запись в БД произведена
1005 | 2202 | 3103 | 3107-MXI-46401A | SDO0001-01 | 3107-MXI-46401A |  | 3107-Z-6421, 3107-Z-6451, 3102-Z-6290, 3107-Z-6493, 3107-Z-6497 | 3107-MXI-46401A | SIS стоп цирк. насоса горячего HTF 3107-HOP-6401A | Hot HTF Circulation Pump 3107-HOP-6401A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6409 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 11 | [12 empty] | Запись в БД произведена
1007 | 2202 | 3103 | 3107-MXI-56401A | SDO0001-01 | 3107-MXI-56401A |  | 3107-Z-6421, 3107-Z-6451, 3102-Z-6290, 3107-Z-6493, 3107-Z-6497 | 3107-MXI-56401A | SIS стоп цирк. насоса горячего HTF 3107-HOP-6401B | Hot HTF Circulation Pump 3107-HOP-6401B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6409 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 4 | [12 empty] | Запись в БД произведена
1009 | 2202 | 3103 | 3107-MXI-66401A | SDO0001-01 | 3107-MXI-66401A |  | 3107-Z-6421, 3107-Z-6451, 3102-Z-6290, 3107-Z-6493, 3107-Z-6497 | 3107-MXI-66401A | SIS стоп цирк. насоса горячего HTF 3107-HOP-6401C | Hot HTF Circulation Pump 3107-HOP-6401C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6409 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 28 | [12 empty] | Запись в БД произведена
1011 | 3108 | 3108 | 3107-LZIA-64003 | SAI1000-01R | 3107-LZIA-64003 |  | 3107-Z-6403 | 3107-LZT-64003 | Уровень в 3107-V-6403 | 3107-V-6403 Liquid level indication | Displacer Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6410 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤2 | 0 | 3100 | mm | 0 | 100 | % | 6,129032 | 17,09677 | 66,45161 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3108-S-JB-C429/3000-S-MC-B03 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 459 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C429 |  |  | 3107-LZT-64003/3108-S-JB-C429 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 5 | [12 empty] | Запись в БД произведена
1013 | 3108 | 3108 | 3107-LZSA-64102 | SDI0010-01R | 3107-LZSA-64102 |  | 3107-Z-6403 | 3107-LZS-64102 | Ур. на выходе 3107-HOP-6402 | 3107-HOP-6402 outlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6410 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C426/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 459 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C426 |  |  | 3107-LZS-64102/3108-S-JB-C426 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 9 | [12 empty] | Запись в БД произведена
1015 | 3108 | 3108 | 3107-TZIA-66369 | SAI1000-01R | 3107-TZIA-66369 |  | 3107-Z-6403 | 3107-TZT-66369 | Т подшипника 3107-HOP-6402 | 3107-HOP-6402 Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6410 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 80 |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3108-S-JB-C429/3000-S-MC-B03 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 459 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C429 |  |  | 3107-TZT-66369/3108-S-JB-C429 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 6 | [12 empty] | Запись в БД произведена
1016 | 2202 | 3108 | 3107-MXI-46402A | SDO0001-01 | 3107-MXI-46402A |  | 3107-Z-6403, 3108-Z-6190 | 3107-MXI-46402A | SIS стоп насоса подачи HTF 3107-HOP-6402 | HTF Delivery Pump 3107-HOP-6402 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6410 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 12 | [12 empty] | Запись в БД произведена
1018 | 3103 | 3103 | 3107-LZSA-64014A | SDI0010-01R | 3107-LZSA-64014A |  | 3107-Z-6422 | 3107-LZS-64014A | Ур. на входе 3107-HOP-6414A | 3107-HOP-6414A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C198/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C198 |  |  | 3107-LZS-64014A/3103-S-JB-C198 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 16 | [12 empty] | Запись в БД произведена
1020 | 3103 | 3103 | 3107-LZSA-64014B | SDI0010-01R | 3107-LZSA-64014B |  | 3107-Z-6422 | 3107-LZS-64014B | Ур. на входе 3107-HOP-6414B | 3107-HOP-6414B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C203/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 482 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C203 |  |  | 3107-LZS-64014B/3103-S-JB-C203 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 21 | [12 empty] | Запись в БД произведена
1022 | 3103 | 3103 | 3107-XZV-64127 | SKLPD0021-00 | 3107-XZV-64127 |  |  | 3107-XZV-64127 | Отс. клап. на входе 3107-HOP-6414A | 3107-HOP-6414A Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1023 | 3103 | 3103 | 3107-XZV-64127 | SKLPD0021-00 | 3107-XZV-64127 |  | 3107-Z-6464 | 3107-XZY-64127 | Отс. клап. на входе 3107-HOP-6414A | 3107-HOP-6414A Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR08 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64127/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 8 | [12 empty] | Запись в БД произведена
1024 | 3103 | 3103 | 3107-XZV-64127 | SKLPD0021-00 | 3107-XZV-64127 |  |  | 3107-XZZSC-64127 | Отс. клап. на входе 3107-HOP-6414A (закрыт) | 3107-HOP-6414A Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3107-XZZSC-64127/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 28 | [12 empty] | Запись в БД произведена
1025 | 3103 | 3103 | 3107-XZV-64127 | SKLPD0021-00 | 3107-XZV-64127 |  |  | 3107-XZZSO-64127 | Отс. клап. на входе 3107-HOP-6414A (открыт) | 3107-HOP-6414A Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3107-XZZSO-64127/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 10 | - | A21-10 | - | A22-10 | - | 0 | [12 empty] | Запись в БД произведена
1027 | 3103 | 3103 | 3107-XZV-64128 | SKLPD0021-00 | 3107-XZV-64128 |  |  | 3107-XZV-64128 | Отс. клап. на выходе 3107-HOP-6414A | 3107-HOP-6414A Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1028 | 3103 | 3103 | 3107-XZV-64128 | SKLPD0021-00 | 3107-XZV-64128 |  | 3107-Z-6464 | 3107-XZY-64128 | Отс. клап. на выходе 3107-HOP-6414A | 3107-HOP-6414A Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR09 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64128/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 9 | [12 empty] | Запись в БД произведена
1029 | 3103 | 3103 | 3107-XZV-64128 | SKLPD0021-00 | 3107-XZV-64128 |  |  | 3107-XZZSC-64128 | Отс. клап. на выходе 3107-HOP-6414A (закрыт) | 3107-HOP-6414A Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3107-XZZSC-64128/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 29 | [12 empty] | Запись в БД произведена
1030 | 3103 | 3103 | 3107-XZV-64128 | SKLPD0021-00 | 3107-XZV-64128 |  |  | 3107-XZZSO-64128 | Отс. клап. на выходе 3107-HOP-6414A (открыт) | 3107-HOP-6414A Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3107-XZZSO-64128/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 10 | - | A21-10 | - | A22-10 | - | 1 | [12 empty] | Запись в БД произведена
1032 | 3103 | 3103 | 3107-XZV-64129 | SKLPD0021-00 | 3107-XZV-64129 |  |  | 3107-XZV-64129 | Отс. клап. на входе 3107-HOP-6414B | 3107-HOP-6414B Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1033 | 3103 | 3103 | 3107-XZV-64129 | SKLPD0021-00 | 3107-XZV-64129 |  | 3107-Z-6465 | 3107-XZY-64129 | Отс. клап. на входе 3107-HOP-6414B | 3107-HOP-6414B Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR10 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64129/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 10 | [12 empty] | Запись в БД произведена
1034 | 3103 | 3103 | 3107-XZV-64129 | SKLPD0021-00 | 3107-XZV-64129 |  |  | 3107-XZZSC-64129 | Отс. клап. на входе 3107-HOP-6414B (закрыт) | 3107-HOP-6414B Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3107-XZZSC-64129/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 30 | [12 empty] | Запись в БД произведена
1035 | 3103 | 3103 | 3107-XZV-64129 | SKLPD0021-00 | 3107-XZV-64129 |  |  | 3107-XZZSO-64129 | Отс. клап. на входе 3107-HOP-6414B (открыт) | 3107-HOP-6414B Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3107-XZZSO-64129/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 10 | - | A21-10 | - | A22-10 | - | 2 | [12 empty] | Запись в БД произведена
1037 | 3103 | 3103 | 3107-XZV-64130 | SKLPD0021-00 | 3107-XZV-64130 |  |  | 3107-XZV-64130 | Отс. клап. на выходе 3107-HOP-6414B | 3107-HOP-6414B Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1038 | 3103 | 3103 | 3107-XZV-64130 | SKLPD0021-00 | 3107-XZV-64130 |  | 3107-Z-6465 | 3107-XZY-64130 | Отс. клап. на выходе 3107-HOP-6414B | 3107-HOP-6414B Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-D213/3000-S-MC-B12 | PR11 | NH-KYJYP3 37x2.5 | 472 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3103-S-JB-D213 |  |  | 3107-XZY-64130/3103-S-JB-D213 | 3000-S-SC-B02 | 3000-S-MC-B14 |  | A23 | A24 | 04 | 05 | A23-04 | A23-05 | A24-04 | A24-05 | 11 | [12 empty] | Запись в БД произведена
1039 | 3103 | 3103 | 3107-XZV-64130 | SKLPD0021-00 | 3107-XZV-64130 |  |  | 3107-XZZSC-64130 | Отс. клап. на выходе 3107-HOP-6414B (закрыт) | 3107-HOP-6414B Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3107-XZZSC-64130/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 11 | - | A21-11 | - | A22-11 | - | 31 | [12 empty] | Запись в БД произведена
1040 | 3103 | 3103 | 3107-XZV-64130 | SKLPD0021-00 | 3107-XZV-64130 |  |  | 3107-XZZSO-64130 | Отс. клап. на выходе 3107-HOP-6414B (открыт) | 3107-HOP-6414B Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-6411 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3103-S-JB-C212/3000-S-MC-B06 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 500 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3103-S-JB-C212 |  |  | 3107-XZZSO-64130/3103-S-JB-C212 | 3000-S-SC-B02 | 3000-S-MC-B06 |  | A21 | A22 | 10 | - | A21-10 | - | A22-10 | - | 3 | [12 empty] | Запись в БД произведена
1042 | 2202 | 3103 | 3107-MXI-46414A | SDO0001-01 | 3107-MXI-46414A |  | 3107-Z-6422, 3107-Z-6464, 3103-Z-6292 | 3107-MXI-46414A | SIS стоп насоса HTF теплообменника расплава 3107-HOP-6414A | Melt Heat Exchanger HTF Pump 3107-HOP-6414A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6411 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 24 | [12 empty] | Запись в БД произведена
1044 | 2202 | 3103 | 3107-MXI-56414A | SDO0001-01 | 3107-MXI-56414A |  | 3107-Z-6422, 3107-Z-6465, 3103-Z-6292 | 3107-MXI-56414A | SIS стоп насоса HTF теплообменника расплава 3107-HOP-6414B | Melt Heat Exchanger HTF Pump 3107-HOP-6414B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6411 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 15 | [12 empty] | Запись в БД произведена
1046 | 3107 |  | 3107-XZV-64009 | SKLPD0021-00 | 3107-XZV-64009 |  |  | 3107-XZV-64009 | Отс. клап. печи горячего масла | Hot Oil Furnace Shut-off Valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
1047 | 3107 | 3107 | 3107-XZV-64009 | SKLPD0021-00 | 3107-XZV-64009 |  | 3107-Z-6466, 3107-Z-6499 | 3107-XZY-64009 | Отс. клап. печи горячего масла | Hot Oil Furnace Shut-off Valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-D413/3000-S-MC-B14 | PR06 | NH-KYJYP3 16x2.5 | 436 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D413 |  |  | 3107-XZY-64009/3107-S-JB-D413 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 3 | [12 empty] | Запись в БД произведена
1048 | 3107 | 3107 | 3107-XZV-64009 | SKLPD0021-00 | 3107-XZV-64009 |  |  | 3107-XZZSC-64009 | Отс. клап. печи горячего масла (закрыт) | Hot Oil Furnace Shut-off Valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSC-64009/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 0 | [12 empty] | Запись в БД произведена
1049 | 3107 | 3107 | 3107-XZV-64009 | SKLPD0021-00 | 3107-XZV-64009 |  |  | 3107-XZZSO-64009 | Отс. клап. печи горячего масла (открыт) | Hot Oil Furnace Shut-off Valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSO-64009/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 6 | [12 empty] | Запись в БД произведена
1051 | 3107 |  | 3107-XZV-64010 | SKLPD0021-00 | 3107-XZV-64010 |  |  | 3107-XZV-64010 | Азот к 3107-HF-6401 | Nitrogen to 3107-HF-6401 | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
1052 | 3107 | 3107 | 3107-XZV-64010 | SKLPD0021-00 | 3107-XZV-64010 |  | 3107-Z-6466 | 3107-XZY-64010 | Азот к 3107-HF-6401 | Nitrogen to 3107-HF-6401 | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-D407/3000-S-MC-B13 | PR05 | NH-KYJYP3 16x2.5 | 447 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D407 |  |  | 3107-XZY-64010/3107-S-JB-D407 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 1 | [12 empty] | Запись в БД произведена
1053 | 3107 | 3107 | 3107-XZV-64010 | SKLPD0021-00 | 3107-XZV-64010 |  |  | 3107-XZZSC-64010 | Азот к 3107-HF-6401 (закрыт) | Nitrogen to 3107-HF-6401 | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSC-64010/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 1 | [12 empty] | Запись в БД произведена
1054 | 3107 | 3107 | 3107-XZV-64010 | SKLPD0021-00 | 3107-XZV-64010 |  |  | 3107-XZZSO-64010 | Азот к 3107-HF-6401 (открыт) | Nitrogen to 3107-HF-6401 | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSO-64010/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 7 | [12 empty] | Запись в БД произведена
1056 | 3107 |  | 3107-XZV-64011 | SKLPD0021-00 | 3107-XZV-64011 |  |  | 3107-XZV-64011 | Дренаж теплоносителя из 3107-HF-6401 | Heat transfer oil drain from 3107-HF-6401 | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
1057 | 3107 | 3107 | 3107-XZV-64011 | SKLPD0021-00 | 3107-XZV-64011 |  | 3107-Z-6466 | 3107-XZY-64011 | Дренаж теплоносителя из 3107-HF-6401 | Heat transfer oil drain from 3107-HF-6401 | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-XZY-64011/3000-S-MC-B11 |  | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B11 | Одиночный |  | 3107-XZY-64011/3000-S-MC-B11 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 30 | [12 empty] | Запись в БД произведена
1058 | 3107 | 3107 | 3107-XZV-64011 | SKLPD0021-00 | 3107-XZV-64011 |  |  | 3107-XZZSC-64011 | Дренаж теплоносителя из 3107-HF-6401 (закрыт) | Heat transfer oil drain from 3107-HF-6401 | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSC-64011/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 2 | [12 empty] | Запись в БД произведена
1059 | 3107 | 3107 | 3107-XZV-64011 | SKLPD0021-00 | 3107-XZV-64011 |  |  | 3107-XZZSO-64011 | Дренаж теплоносителя из 3107-HF-6401 (открыт) | Heat transfer oil drain from 3107-HF-6401 | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSO-64011/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 8 | [12 empty] | Запись в БД произведена
1061 | 3107 | 3107 | 3107-TZIA-64503A | SAI1000-01R | 3107-TZIA-64503A |  | 3107-Z-6491, 3107-Z-6493 | 3107-TZT-64503A | Т теплоносителя на выходе (Блок.) | Heat transfer oil outlet temperature(Interlock) | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C751/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C751 |  |  | 3107-TZT-64503A/3107-S-JB-C751 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 2 | [12 empty] | Запись в БД произведена
1062 | 3107 | 3107 | 3107-TZIA-64503B | SAI1000-01R | 3107-TZIA-64503B |  | 3107-Z-6491, 3107-Z-6493 | 3107-TZT-64503B | Т теплоносителя на выходе (Блок.) | Heat transfer oil outlet temperature(Interlock) | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C752/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C752 |  |  | 3107-TZT-64503B/3107-S-JB-C752 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 9 | [12 empty] | Запись в БД произведена
1063 | 3107 | 3107 | 3107-TZIA-64503C | SAI1000-01R | 3107-TZIA-64503C |  | 3107-Z-6491, 3107-Z-6493 | 3107-TZT-64503C | Т теплоносителя на выходе (Блок.) | Heat transfer oil outlet temperature(Interlock) | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C753/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C753 |  |  | 3107-TZT-64503C/3107-S-JB-C753 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 0 | [12 empty] | Запись в БД произведена
1065 | 3107 | 3107 | 3107-TZIA-64505A | SAI1000-01R | 3107-TZIA-64505A |  | 3107-Z-6491, 3107-Z-6493, 3107-Z-6497 | 3107-TZT-64505A | Т дымовых газов на выходе печи | Furnace outlet exhaust temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 340 | 370 |  | ℃ |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C751/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C751 |  |  | 3107-TZT-64505A/3107-S-JB-C751 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 3 | [12 empty] | Запись в БД произведена
1066 | 3107 | 3107 | 3107-TZIA-64505B | SAI1000-01R | 3107-TZIA-64505B |  | 3107-Z-6491, 3107-Z-6493, 3107-Z-6497 | 3107-TZT-64505B | Т дымовых газов на выходе печи | Furnace outlet exhaust temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 340 | 370 |  | ℃ |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C752/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C752 |  |  | 3107-TZT-64505B/3107-S-JB-C752 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 10 | [12 empty] | Запись в БД произведена
1067 | 3107 | 3107 | 3107-TZIA-64505C | SAI1000-01R | 3107-TZIA-64505C |  | 3107-Z-6491, 3107-Z-6493, 3107-Z-6497 | 3107-TZT-64505C | Т дымовых газов на выходе печи | Furnace outlet exhaust temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 340 | 370 |  | ℃ |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C753/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C753 |  |  | 3107-TZT-64505C/3107-S-JB-C753 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 1 | [12 empty] | Запись в БД произведена
1069 | 3107 | 3107 | 3107-PZIA-64502A | SAI1000-01R | 3107-PZIA-64502A |  | new 3107-Z-6491, 3107-Z-6496 | 3107-PZT-64502A | Р ПГ перед горелкой | NG Pressure before entering the burner | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 260 | kPaG | 0 | 260 | kPaG | 2 | 3 | 105 | 115 |  | kPaG |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C751/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C751 |  |  | 3107-PZT-64502A/3107-S-JB-C751 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 14 | [12 empty] | Запись в БД произведена
1070 | 3107 | 3107 | 3107-PZIA-64502B | SAI1000-01R | 3107-PZIA-64502B |  | new 3107-Z-6491, 3107-Z-6496 | 3107-PZT-64502B | Р ПГ перед горелкой | NG Pressure before entering the burner | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 260 | kPaG | 0 | 260 | kPaG | 2 | 3 | 105 | 115 |  | kPaG |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C752/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C752 |  |  | 3107-PZT-64502B/3107-S-JB-C752 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 6 | [12 empty] | Запись в БД произведена
1071 | 3107 | 3107 | 3107-PZIA-64502C | SAI1000-01R | 3107-PZIA-64502C |  | new 3107-Z-6491, 3107-Z-6496 | 3107-PZT-64502C | Р ПГ перед горелкой | NG Pressure before entering the burner | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 260 | kPaG | 0 | 260 | kPaG | 2 | 3 | 105 | 115 |  | kPaG |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C753/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C753 |  |  | 3107-PZT-64502C/3107-S-JB-C753 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 13 | [12 empty] | Запись в БД произведена
1073 | 3107 | 3107 | [5 empty] | 3107-FZE-64503A | Расход теплоносителя | Heat transfer oil flow | Measure Orifice |  |  | 2490157-3000-PR007-6401 | Field |  |  | SIS | [17 empty] | 3107-PK-6401 | ИД 2026 07 03
1074 | 3107 | 3107 | 3107-FZIA-64503A | SAI1000-01R | 3107-FZIA-64503A |  | 3107-Z-6491 | 3107-FZT-64503A | Расход теплоносителя | Heat transfer oil flow | D/P Flow Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 300 | m3/h | 0 | 300 | m3/h | 145 | 155 |  |  |  | m3/h |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C751/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C751 |  |  | 3107-FZT-64503A/3107-S-JB-C751 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 13 | [12 empty] | Запись в БД произведена
1075 | 3107 | 3107 | 3107-FZIA-64503B | SAI1000-01R | 3107-FZIA-64503B |  | 3107-Z-6491 | 3107-FZT-64503B | Расход теплоносителя | Heat transfer oil flow | D/P Flow Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 300 | m3/h | 0 | 300 | m3/h | 145 | 155 |  |  |  | m3/h |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C752/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C752 |  |  | 3107-FZT-64503B/3107-S-JB-C752 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 5 | [12 empty] | Запись в БД произведена
1076 | 3107 | 3107 | 3107-FZIA-64503C | SAI1000-01R | 3107-FZIA-64503C |  | 3107-Z-6491 | 3107-FZT-64503C | Расход теплоносителя | Heat transfer oil flow | D/P Flow Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 300 | m3/h | 0 | 300 | m3/h | 145 | 155 |  |  |  | m3/h |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C753/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C753 |  |  | 3107-FZT-64503C/3107-S-JB-C753 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 12 | [12 empty] | Запись в БД произведена
1078 | 3107 | 3107 | 3107-PZIA-64506A | SAI1000-01R | 3107-PZIA-64506A |  | 3107-Z-6466, 3107-Z-6491, 3107-Z-6497 | 3107-PZT-64506A | Р на выходе печи теплоносителя | Outlet pressure of thermal oil furnace | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 1,2 | MPaG | 0 | 1,2 | MPaG | 0,3 | 0,35 |  |  |  | MPaG |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C751/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C751 |  |  | 3107-PZT-64506A/3107-S-JB-C751 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 1 | [12 empty] | Запись в БД произведена
1079 | 3107 | 3107 | 3107-PZIA-64506B | SAI1000-01R | 3107-PZIA-64506B |  | 3107-Z-6466, 3107-Z-6491, 3107-Z-6497 | 3107-PZT-64506B | Р на выходе печи теплоносителя | Outlet pressure of thermal oil furnace | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 1,2 | MPaG | 0 | 1,2 | MPaG | 0,3 | 0,35 |  |  |  | MPaG |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C752/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C752 |  |  | 3107-PZT-64506B/3107-S-JB-C752 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 8 | [12 empty] | Запись в БД произведена
1080 | 3107 | 3107 | 3107-PZIA-64506C | SAI1000-01R | 3107-PZIA-64506C |  | 3107-Z-6466, 3107-Z-6491, 3107-Z-6497 | 3107-PZT-64506C | Р на выходе печи теплоносителя | Outlet pressure of thermal oil furnace | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 1,2 | MPaG | 0 | 1,2 | MPaG | 0,3 | 0,35 |  |  |  | MPaG |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C753/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C753 |  |  | 3107-PZT-64506C/3107-S-JB-C753 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 14 | [12 empty] | Запись в БД произведена
1082 | 3107 | 3107 | 3107-TZIA-64511 | SAI1000-01R | 3107-TZIA-64511 |  | 3107-Z-6491 | 3107-TZT-64511 | Т змеевика теплоносителя | Heat conduction oil coil temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C751/3000-S-MC-B01 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C751 |  |  | 3107-TZT-64511/3107-S-JB-C751 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 4 | [12 empty] | Запись в БД произведена
1084 | 3107 | 3107 | 3107-TZIA-64512 | SAI1000-01R | 3107-TZIA-64512 |  | 3107-Z-6491 | 3107-TZT-64512 | Т змеевика теплоносителя | Heat conduction oil coil temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C752/3000-S-MC-B01 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C752 |  |  | 3107-TZT-64512/3107-S-JB-C752 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 11 | [12 empty] | Запись в БД произведена
1086 | 3107 | 3107 | 3107-TZIA-64513 | SAI1000-01R | 3107-TZIA-64513 |  | 3107-Z-6491 | 3107-TZT-64513 | Т змеевика теплоносителя | Heat conduction oil coil temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C753/3000-S-MC-B01 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C753 |  |  | 3107-TZT-64513/3107-S-JB-C753 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 2 | [12 empty] | Запись в БД произведена
1088 | 3107 | 3107 | 3107-PZIA-64503 | SAI1000-01R | 3107-PZIA-64503 |  | 3107-Z-6491 | 3107-PZT-64503 | Р холодного воздуха на выходе вентилятора | Blower outlet cold air pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 12 | kPaG | 0 | 12 | kPaG | 0.2 | 0.3 |  |  |  | kPaG |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C751/3000-S-MC-B01 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C751 |  |  | 3107-PZT-64503/3107-S-JB-C751 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 0 | [12 empty] | Запись в БД произведена
1090 | 3107 | 3107 | 3107-PZIA-64504 | SAI1000-01R | 3107-PZIA-64504 |  | 3107-Z-6491 | 3107-PZT-64504 | Р холодного воздуха на выходе вентилятора | Blower outlet cold air pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 12 | kPaG | 0 | 12 | kPaG | 0.2 | 0.3 |  |  |  | kPaG |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C752/3000-S-MC-B01 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C752 |  |  | 3107-PZT-64504/3107-S-JB-C752 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 7 | [12 empty] | Запись в БД произведена
1092 | 3107 | 3107 | 3107-AZIA-64502 | SAI1000-01R | 3107-AZIA-64502 |  | new 3107-Z-6492, 3107-Z-6497 | 3107-AZT-64502 | Анализатор O2 в дымовых газах | Flue gas oxygen analyzer | O2 analyzer transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | AIR-EP | Exd | SIS | I | 230V AC 4-wire external Power | 0,48 | 0 | 25 | % | 0 | 25 | % | 0.5 | 2 |  |  |  | % |  |  | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-AZT-64502/3000-S-MC-B04 |  | NH-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B04 | Одиночный |  | 3107-AZT-64502/3000-S-MC-B04 | 3000-S-SC-B03 | 3000-S-MC-B04 |  | A31 | A32 | 06 | - | A31-06 | - | A32-06 | - | 0 | [12 empty] | Запись в БД произведена
1094 | 3107 | 3107 | 3107-B-64501 |  |  |  | 3107-Z-6491, 3107-Z-6494 | 3107-BZE-64501 | Сигнал пламени | Flame signal | Ultraviolet flame detector | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B755/3000-S-MC-B11-01 |  | NH-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B11 | Одиночный |  | 3107-S-JB-B755/3000-S-MC-B11-01 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 16 | [12 empty] | Запись в БД произведена
1095 | 3107 | 3107 | 3107-B-64502 |  |  |  | 3107-Z-6491, 3107-Z-6494 | 3107-BZE-64502 | Сигнал пламени | Flame signal | Ultraviolet flame detector | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B755/3000-S-MC-B11-02 |  | NH-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B11 | Одиночный |  | 3107-S-JB-B755/3000-S-MC-B11-02 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 17 | [12 empty] | Запись в БД произведена
1097 | 3107 | 3107 | 3107-XZV-64501 | SKLPD0021-00 | 3107-XZV-64501 |  |  | 3107-XZV-64501 | Отс. клап. магистрали ПГ A | NG main On-off valve A | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field |  |  | SIS | [17 empty] | 3107-PK-6401 | ИД 2026 07 03
1098 | 3107 | 3107 | 3107-XZV-64501 | SKLPD0021-00 | 3107-XZV-64501 |  | 3107-Z-6491, 3107-Z-6492, 3107-Z-6493, 3107-Z-6496, 3107-Z-6497, 3107-Z-6499 | 3107-XZY-64501 | Отс. клап. магистрали ПГ A | NG main On-off valve A | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B754/3000-S-MC-B13-02 | PR01 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B754 |  |  | 3107-XZY-64501/3107-S-JB-B754 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 18 | [12 empty] | Запись в БД произведена
1099 | 3107 | 3107 | 3107-XZV-64501 | SKLPD0021-00 | 3107-XZV-64501 |  |  | 3107-XZZSO-64501 | Отс. клап. магистрали ПГ A (открыт) | NG main On-off valve A | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSO-64501/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 23 | [12 empty] | Запись в БД произведена
1100 | 3107 | 3107 | 3107-XZV-64501 | SKLPD0021-00 | 3107-XZV-64501 |  |  | 3107-XZZSC-64501 | Отс. клап. магистрали ПГ A (закрыт) | NG main On-off valve A | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSC-64501/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 17 | [12 empty] | Запись в БД произведена
1102 | 3107 | 3107 | 3107-XZV-64502 | SKLPD0021-00 | 3107-XZV-64502 |  |  | 3107-XZV-64502 | Отс. клап. магистрали ПГ B | NG main On-off valve B | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field |  |  | SIS | [17 empty] | 3107-PK-6401 | ИД 2026 07 03
1103 | 3107 | 3107 | 3107-XZV-64502 | SKLPD0021-00 | 3107-XZV-64502 |  | 3107-Z-6491, 3107-Z-6492, 3107-Z-6493, 3107-Z-6497 | 3107-XZY-64502 | Отс. клап. магистрали ПГ B | NG main On-off valve B | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B754/3000-S-MC-B13-02 | PR02 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B754 |  |  | 3107-XZY-64502/3107-S-JB-B754 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 19 | [12 empty] | Запись в БД произведена
1104 | 3107 | 3107 | 3107-XZV-64502 | SKLPD0021-00 | 3107-XZV-64502 |  |  | 3107-XZZSO-64502 | Отс. клап. магистрали ПГ B (открыт) | NG main On-off valve B | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSO-64502/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 24 | [12 empty] | Запись в БД произведена
1105 | 3107 | 3107 | 3107-XZV-64502 | SKLPD0021-00 | 3107-XZV-64502 |  |  | 3107-XZZSC-64502 | Отс. клап. магистрали ПГ B (закрыт) | NG main On-off valve B | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSC-64502/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 18 | [12 empty] | Запись в БД произведена
1107 | 3107 | 3107 | 3107-XZV-64503 | SKLPD0021-00 | 3107-XZV-64503 |  |  | 3107-XZV-64503 | Клапан сброса магистрали ПГ | NG main vent valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field |  |  | SIS | [17 empty] | 3107-PK-6401 | ИД 2026 07 03
1108 | 3107 | 3107 | 3107-XZV-64503 | SKLPD0021-00 | 3107-XZV-64503 |  | 3107-Z-6491, 3107-Z-6492, 3107-Z-6493, 3107-Z-6496, 3107-Z-6497 | 3107-XZY-64503 | Клапан сброса магистрали ПГ | NG main vent valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B754/3000-S-MC-B13-02 | PR03 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B754 |  |  | 3107-XZY-64503/3107-S-JB-B754 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 20 | [12 empty] | Запись в БД произведена
1109 | 3107 | 3107 | 3107-XZV-64503 | SKLPD0021-00 | 3107-XZV-64503 |  |  | 3107-XZZSO-64503 | Клапан сброса магистрали ПГ (открыт) | NG main vent valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSO-64503/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 25 | [12 empty] | Запись в БД произведена
1110 | 3107 | 3107 | 3107-XZV-64503 | SKLPD0021-00 | 3107-XZV-64503 |  |  | 3107-XZZSC-64503 | Клапан сброса магистрали ПГ (закрыт) | NG main vent valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSC-64503/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 19 | [12 empty] | Запись в БД произведена
1112 | 3107 | 3107 | 3107-XZV-64504 | SKLPD0021-00 | 3107-XZV-64504 |  |  | 3107-XZV-64504 | Отс. клап. линии зажигания ПГ A | NG Ignition path On-off valve A | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field |  |  | SIS | [17 empty] | 3107-PK-6401 | ИД 2026 07 03
1113 | 3107 | 3107 | 3107-XZV-64504 | SKLPD0021-00 | 3107-XZV-64504 |  | new 3107-Z-6492, 3107-Z-6491, 3107-Z-6493, 3107-Z-6494, 3107-Z-6497, 3107-Z-6499 | 3107-XZY-64504 | Отс. клап. линии зажигания ПГ A | NG Ignition path On-off valve A | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B754/3000-S-MC-B13-02 | PR04 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B754 |  |  | 3107-XZY-64504/3107-S-JB-B754 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 21 | [12 empty] | Запись в БД произведена
1114 | 3107 | 3107 | 3107-XZV-64504 | SKLPD0021-00 | 3107-XZV-64504 |  |  | 3107-XZZSO-64504 | Отс. клап. линии зажигания ПГ A (открыт) | NG Ignition path On-off valve A | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSO-64504/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 26 | [12 empty] | Запись в БД произведена
1115 | 3107 | 3107 | 3107-XZV-64504 | SKLPD0021-00 | 3107-XZV-64504 |  |  | 3107-XZZSC-64504 | Отс. клап. линии зажигания ПГ A (закрыт) | NG Ignition path On-off valve A | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSC-64504/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 20 | [12 empty] | Запись в БД произведена
1117 | 3107 | 3107 | 3107-XZV-64505 | SKLPD0021-00 | 3107-XZV-64505 |  |  | 3107-XZV-64505 | Отс. клап. линии зажигания ПГ B | NG Ignition path On-off valve B | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field |  |  | SIS | [17 empty] | 3107-PK-6401 | ИД 2026 07 03
1118 | 3107 | 3107 | 3107-XZV-64505 | SKLPD0021-00 | 3107-XZV-64505 |  | 3107-Z-6491, 3107-Z-6492, 3107-Z-6493, 3107-Z-6494, 3107-Z-6497 | 3107-XZY-64505 | Отс. клап. линии зажигания ПГ B | NG Ignition path On-off valve B | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B754/3000-S-MC-B13-02 | PR05 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B754 |  |  | 3107-XZY-64505/3107-S-JB-B754 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 22 | [12 empty] | Запись в БД произведена
1119 | 3107 | 3107 | 3107-XZV-64505 | SKLPD0021-00 | 3107-XZV-64505 |  |  | 3107-XZZSO-64505 | Отс. клап. линии зажигания ПГ B (открыт) | NG Ignition path On-off valve B | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSO-64505/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 27 | [12 empty] | Запись в БД произведена
1120 | 3107 | 3107 | 3107-XZV-64505 | SKLPD0021-00 | 3107-XZV-64505 |  |  | 3107-XZZSC-64505 | Отс. клап. линии зажигания ПГ B (закрыт) | NG Ignition path On-off valve B | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSC-64505/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 21 | [12 empty] | Запись в БД произведена
1122 | 3107 | 3107 | 3107-XZV-64506 | SKLPD0021-00 | 3107-XZV-64506 |  |  | 3107-XZV-64506 | Клапан сброса линии зажигания ПГ | NG Ignition path vent valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field |  |  | SIS | [17 empty] | 3107-PK-6401 | ИД 2026 07 03
1123 | 3107 | 3107 | 3107-XZV-64506 | SKLPD0021-00 | 3107-XZV-64506 |  | new 3107-Z-6492, 3107-Z-6491, 3107-Z-6493, 3107-Z-6494, 3107-Z-6497 | 3107-XZY-64506 | Клапан сброса линии зажигания ПГ | NG Ignition path vent valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B754/3000-S-MC-B13-02 | PR06 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B754 |  |  | 3107-XZY-64506/3107-S-JB-B754 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 23 | [12 empty] | Запись в БД произведена
1124 | 3107 | 3107 | 3107-XZV-64506 | SKLPD0021-00 | 3107-XZV-64506 |  |  | 3107-XZZSO-64506 | Клапан сброса линии зажигания ПГ (открыт) | NG Ignition path vent valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSO-64506/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 28 | [12 empty] | Запись в БД произведена
1125 | 3107 | 3107 | 3107-XZV-64506 | SKLPD0021-00 | 3107-XZV-64506 |  |  | 3107-XZZSC-64506 | Клапан сброса линии зажигания ПГ (закрыт) | NG Ignition path vent valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C757/3000-S-MC-B05 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C757 |  |  | 3107-XZZSC-64506/3107-S-JB-C757 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 22 | [12 empty] | Запись в БД произведена
1127 | 3107 | 3107 | 3107-BZI-64501 | SDO0001-01 | 3107-BZI-64501 |  | #N/A | 3107-BZI-64501 | Сигнал работы трансформатора зажигания | Ignition transformer working signal | Ignition transformer | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | 4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B754/3000-S-MC-B13-02 | PR07 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B754 |  |  | 3107-S-JB-B756/3107-S-JB-B754 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 17 | [12 empty] | Запись в БД произведена
1129 | 3107 | 3107 | 3107-HZS-64501 | SDI0010-01R | 3107-HZS-64501 |  | #N/A | 3107-HZS-64501 | Переключатель Местное/Дистанционное (1 сигн.) | Local/remote knob（1 contact signal） | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F01/3000-S-MC-B10-02 | PR04 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F01 |  |  | 3107-HZS-64501/3107-I-LP-F01 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 18 | [12 empty] | Запись в БД произведена
1131 | 3107 | 3107 | 3107-HZS-64502 | SDI0010-01R | 3107-HZS-64502 |  | #N/A | 3107-HZS-64502 | Кнопка Пуск на МЩУ | LCP-Start button | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F01/3000-S-MC-B10-02 | PR05 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F01 |  |  | 3107-HZS-64502/3107-I-LP-F01 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 19 | [12 empty] | Запись в БД произведена
1133 | 3107 | 3107 | 3107-HZS-64503 | SDI0010-01R | 3107-HZS-64503 |  | 3107-Z-6491 | 3107-HZS-64503 | Кнопка Стоп на МЩУ | LCP-Stop button | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F01/3000-S-MC-B10-02 | PR06 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F01 |  |  | 3107-HZS-64503/3107-I-LP-F01 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 20 | [12 empty] | Запись в БД произведена
1135 | 3107 | 3107 | 3107-HZS-64504 | SDI0010-01R | 3107-HZS-64504 |  | #N/A | 3107-HZS-64504 | Кнопка Сброс на МЩУ | LCP-Reset button | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F01/3000-S-MC-B10-02 | PR07 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F01 |  |  | 3107-HZS-64504/3107-I-LP-F01 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 21 | [12 empty] | Запись в БД произведена
1137 | 3107 | 3107 | 3107-HZS-64505_1 | SDI0010-01R | 3107-HZS-64505-1 |  | 3107-Z-6492 | 3107-HZS-64505-1 | Кнопка Авар. останова на МЩУ-1 | LCP-Emergency button-1 | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 8 | [12 empty] | Запись в БД произведена
1139 | 3107 | 3107 | 3107-HZS-64505_2 | SDI0010-01R | 3107-HZS-64505-2 |  | 3107-Z-6492 | 3107-HZS-64505-2 | Кнопка Авар. останова на МЩУ-2 | LCP-Emergency button-2 | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 9 | [12 empty] | Запись в БД произведена
1141 | 3107 | 3107 | 3107-HZS-64505_3 | SDI0010-01R | 3107-HZS-64505-3 |  | 3107-Z-6492 | 3107-HZS-64505-3 | Кнопка Авар. останова на МЩУ-3 | LCP-Emergency button-3 | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 10 | [12 empty] | Запись в БД произведена
1143 | 3107 | 3107 | 3107-XZV-64501 | SKLPD0021-00 | 3107-XZV-64501 |  | #N/A | 3107-XZL-64501 | Лампа Готовность к розжигу на МЩУ | LCP-Ignition ready indicator light | Indicator light: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F01/3000-S-MC-B10-02 | PR01 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F01 |  |  | 3107-XZL-64501/3107-I-LP-F01 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 19 | [12 empty] | Запись в БД произведена
1145 | 3107 | 3107 | 3107-XZV-64502 | SKLPD0021-00 | 3107-XZV-64502 |  | #N/A | 3107-XZL-64502 | Лампа Работа на МЩУ | LCP-Running light | Indicator light: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F01/3000-S-MC-B10-02 | PR02 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F01 |  |  | 3107-XZL-64502/3107-I-LP-F01 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 20 | [12 empty] | Запись в БД произведена
1147 | 3107 | 3107 | 3107-XZV-64503 | SKLPD0021-00 | 3107-XZV-64503 |  | #N/A | 3107-XZL-64503 | Лампа Авария на МЩУ | LCP-Alarm light | Indicator light: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | LCP | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F01/3000-S-MC-B10-02 | PR03 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F01 |  |  | 3107-XZL-64503/3107-I-LP-F01 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 21 | [12 empty] | Запись в БД произведена
1149 | 2202 | 3107 | 3107-MXI-64520B | SDO0001-01 | 3107-MXI-64520B |  | #N/A | 3107-MXI-64520B | SIS пуск вентилятора воздуха горения 3107-BL-6402 | Combustion air blower 3107-BL-6402 SIS Start Command | SIS Start Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6421 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type/Loop No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 27 | [12 empty] | Запись в БД произведена
1151 | 2202 | 3107 | 3107-MXI-64520A | SDO0001-01 | 3107-MXI-64520A |  | new 3107-Z-6492, 3107-Z-6491, 3107-Z-6493, 3107-Z-6494, 3107-Z-6496 | 3107-MXI-64520A | SIS стоп вентилятора воздуха горения 3107-BL-6402 | Combustion air blower 3107-BL-6402 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6421 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type/Loop No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 26 | [12 empty] | Запись в БД произведена
1153 | 2202 | 3107 | 3107-MXA-64520B | SDI0010-01R | 3107-MXA-64520B |  | new 3107-Z-6492, 3107-Z-6497 | 3107-MXA-64520B | Вентилятор воздуха горения 3107-BL-6402 работает | Combustion air blower 3107-BL-6402 Running | Running | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6421 | MCC | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type/Loop No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A70 | A71 | 14 | - | A70-14 | - | A71-14 | - | 0 | [12 empty] | Запись в БД произведена
1155 | 3107 | 3107 | 3107-YZS-64501 | SDO0001-01 | 3107-YZS-64501 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-64501 | 3107-B-6401 Состояние зажигания 1, SIS->DCS | 3107-B-6401 Ignition state 1, SIS to DCS， 3107-B-6401 Состояние зажигания 1, от SIS до DCS | When the furnace is in non-"operating mode”, the blower frequency MV and the main gas valve MV lock the ignition opening； In the "operating mode", the blower frequency MV and the main gas valve MV are unlocked. | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 23 | [12 empty] | Запись в БД произведена
1157 | 3107 | 3107 | 3107-YZS-64502 | SDO0001-01 | 3107-YZS-64502 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-64502 | 3107-B-6401 Состояние зажигания 2, SIS->DCS | 3107-B-6401 Ignition state 2, SIS to DCS， 3107-B-6401 Состояние зажигания 2, от SIS до DCS | The inverter of the blower is set to 0HZ | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 24 | [12 empty] | Запись в БД произведена
1159 | 3107 | 3107 | 3107-YZS-64503 | SDO0001-01 | 3107-YZS-64503 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-64503 | 3107-B-6401 Состояние зажигания 3, SIS->DCS | 3107-B-6401 Ignition state 3, SIS to DCS， 3107-B-6401 Состояние зажигания 3, от SIS до DCS | Air purge stage (Air purge before ignition stage + Air purge after stop stage) Blower frequency setting, purge opening | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 26 | [12 empty] | Запись в БД произведена
1161 | 3107 | 3107 | 3107-YZS-64504 | SDO0001-01 | 3107-YZS-64504 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-64504 | 3107-B-6401, SIS->DCS, закрыть отс. клап. Выхлопа | 3107-B-6401 , SIS to DCS，Close the exhaust gas on-off valve 3107-B-6401 ,Подключите SIS к DCS, закройте клапан включения-выключения выхлопных газов. | Close the exhaust gas on-off valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6421 | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 27 | [12 empty] | Запись в БД произведена
1163 | 3107 | 3107 | 3107-YZS-64505 | SDO0001-01 | 3107-YZS-64505 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-64505 | 3107-B-6401, SIS->DCS, резерв | 3107-B-6401 , SIS to DCS，Spare 3107-B-6401 ,Подключите SIS к DCS, запасной |  | 3000_S_SC_B03 | SCS3 |  | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-6401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 25 | [12 empty] | Запись в БД произведена
1165 | 3109 | 3109 | 3109-LZIA-67102 | SAI1000-01R | 3109-LZIA-67102 |  | 3109-Z-6701 | 3109-LZT-67102 | Ур. в 3109-V-6701, сигн. HH (блок.) | 3109-V-6701 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 9100 | mm | 0 | 100 | % | 5,846154 | 8,131868 | 85,84615 | 97,27473 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3109-LZT-67102/3109-S-JB-C437 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 12 | [12 empty] | Запись в БД произведена
1167 | 3109 | 3109 | 3109-XZV-67101 | SKLPD0021-00 | 3109-XZV-67101 |  |  | 3109-XZV-67101 | V-6701, блок. отсечки | 3109-V-6701 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1168 | 3109 | 3109 | 3109-XZV-67101 | SKLPD0021-00 | 3109-XZV-67101 |  | 3109-Z-6701, 3109-Z-6791, 3000-Z-6295 | 3109-XZY-67101 | V-6701, блок. отсечки | 3109-V-6701 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D444/3000-S-MC-B13 | PR02 | NH-KYJYP3 24x2.5 | 354 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D444 |  |  | 3109-XZY-67101/3109-S-JB-D444 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 13 | [12 empty] | Запись в БД произведена
1169 | 3109 | 3109 | 3109-XZV-67101 | SKLPD0021-00 | 3109-XZV-67101 |  |  | 3109-XZZSC-67101 | V-6701, блок. отсечки (закрыт) | 3109-V-6701 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSC-67101/3109-S-JB-C439 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 0 | [12 empty] | Запись в БД произведена
1170 | 3109 | 3109 | 3109-XZV-67101 | SKLPD0021-00 | 3109-XZV-67101 |  |  | 3109-XZZSO-67101 | V-6701, блок. отсечки (открыт) | 3109-V-6701 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSO-67101/3109-S-JB-C439 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 3 | [12 empty] | Запись в БД произведена
1172 | 3109 | 3109 | 3109-XZV-67102 | SKLPD0021-00 | 3109-XZV-67102 |  |  | 3109-XZV-67102 | P-6701A/B/C, блок. отсечки | 3109-P-6701A/B/C Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1173 | 3109 | 3109 | 3109-XZV-67102 | SKLPD0021-00 | 3109-XZV-67102 |  | 3109-Z-6715 | 3109-XZY-67102 | P-6701A/B/C, блок. отсечки | 3109-P-6701A/B/C Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D444/3000-S-MC-B13 | PR03 | NH-KYJYP3 24x2.5 | 354 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D444 |  |  | 3109-XZY-67102/3109-S-JB-D444 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 14 | [12 empty] | Запись в БД произведена
1174 | 3109 | 3109 | 3109-XZV-67102 | SKLPD0021-00 | 3109-XZV-67102 |  |  | 3109-XZZSC-67102 | P-6701A/B/C, блок. отсечки (закрыт) | 3109-P-6701A/B/C Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSC-67102/3109-S-JB-C439 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 1 | [12 empty] | Запись в БД произведена
1175 | 3109 | 3109 | 3109-XZV-67102 | SKLPD0021-00 | 3109-XZV-67102 |  |  | 3109-XZZSO-67102 | P-6701A/B/C, блок. отсечки (открыт) | 3109-P-6701A/B/C Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSO-67102/3109-S-JB-C439 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 4 | [12 empty] | Запись в БД произведена
1177 | 3109 | 3109 | 3109-XZV-67103 | SKLPD0021-00 | 3109-XZV-67103 |  |  | 3109-XZV-67103 | P-6701A/B/C, блок. отсечки выдачи | 3109-P-6701A/B/C Interlock to cut off the outfeed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1178 | 3109 | 3109 | 3109-XZV-67103 | SKLPD0021-00 | 3109-XZV-67103 |  | 3109-Z-6715, 3109-Z-6791, 3000-Z-6295 | 3109-XZY-67103 | P-6701A/B/C, блок. отсечки выдачи | 3109-P-6701A/B/C Interlock to cut off the outfeed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR03 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3109-XZY-67103/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 3 | [12 empty] | Запись в БД произведена
1179 | 3109 | 3109 | 3109-XZV-67103 | SKLPD0021-00 | 3109-XZV-67103 |  |  | 3109-XZZSC-67103 | P-6701A/B/C, блок. отсечки выдачи (закрыт) | 3109-P-6701A/B/C Interlock to cut off the outfeed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C441/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C441 |  |  | 3109-XZZSC-67103/3109-S-JB-C441 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 22 | [12 empty] | Запись в БД произведена
1180 | 3109 | 3109 | 3109-XZV-67103 | SKLPD0021-00 | 3109-XZV-67103 |  |  | 3109-XZZSO-67103 | P-6701A/B/C, блок. отсечки выдачи (открыт) | 3109-P-6701A/B/C Interlock to cut off the outfeed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C441/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C441 |  |  | 3109-XZZSO-67103/3109-S-JB-C441 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 25 | [12 empty] | Запись в БД произведена
1182 | 3109 | 3109 | 3109-TZIA-66363A | SAI1000-01R | 3109-TZIA-66363A |  | 3109-Z-6715 | 3109-TZT-66363A | Т подшипника 3109-P-6701A | 3109-P-6701A Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3109-TZT-66363A/3000-S-MC-B01 |  | NH-IA-DJYYP3 1x2x1.5 | 328 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B01 | Одиночный |  | 3109-TZT-66363A/3000-S-MC-B01 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 8 | [12 empty] | Запись в БД произведена
1183 | 2202 | 3109 | 3109-MXI-06701A | SDO0001-01 | 3109-MXI-06701A |  | 3109-Z-6701, 3109-Z-6715, 3109-Z-6790 | 3109-MXI-06701A | SIS стоп насоса подачи стирола 3109-P-6701A | STY Feed Pump 3109-P-6701A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6701 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 7 | [12 empty] | Запись в БД произведена
1185 | 3109 | 3109 | 3109-TZIA-66363B | SAI1000-01R | 3109-TZIA-66363B |  | 3109-Z-6715 | 3109-TZT-66363B | Т подшипника 3109-P-6701B | 3109-P-6701B Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3109-TZT-66363B/3000-S-MC-B01 |  | NH-IA-DJYYP3 1x2x1.5 | 328 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B01 | Одиночный |  | 3109-TZT-66363B/3000-S-MC-B01 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 9 | [12 empty] | Запись в БД произведена
1186 | 2202 | 3109 | 3109-MXI-16701A | SDO0001-01 | 3109-MXI-16701A |  | 3109-Z-6701, 3109-Z-6715, 3109-Z-6790 | 3109-MXI-16701A | SIS стоп насоса подачи стирола 3109-P-6701B | STY Feed Pump 3109-P-6701B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6701 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 17 | [12 empty] | Запись в БД произведена
1188 | 3109 | 3109 | 3109-TZIA-66363C | SAI1000-01R | 3109-TZIA-66363C |  | 3109-Z-6715 | 3109-TZT-66363C | Т подшипника 3109-P-6701C | 3109-P-6701C Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6701 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3109-TZT-66363C/3000-S-MC-B01 |  | NH-IA-DJYYP3 1x2x1.5 | 328 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B01 | Одиночный |  | 3109-TZT-66363C/3000-S-MC-B01 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 10 | [12 empty] | Запись в БД произведена
1189 | 2202 | 3109 | 3109-MXI-26701A | SDO0001-01 | 3109-MXI-26701A |  | 3109-Z-6701, 3109-Z-6715, 3109-Z-6790 | 3109-MXI-26701A | SIS стоп насоса подачи стирола 3109-P-6701C | STY Feed Pump 3109-P-6701C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6701 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 24 | [12 empty] | Запись в БД произведена
1191 | 3109 | 3109 | 3109-LZIA-67202 | SAI1000-01R | 3109-LZIA-67202 |  | 3109-Z-6702 | 3109-LZT-67202 | Ур. в 3109-V-6702, сигн. HH (блок.) | 3109-V-6702 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6702 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6500 | mm | 0 | 100 | % | 4,738462 | 7,076923 | 85,41538 | 97,10769 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3109-LZT-67202/3109-S-JB-C437 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 11 | [12 empty] | Запись в БД произведена
1193 | 3109 | Сombined Title | 3109-PZIA-67204 | SAI1000-01R | 3109-PZIA-67204 |  | 3102-Z-6203, 3102-Z-6208, 3104-Z-7203, 3104-Z-7208 | 3109-PZT-67204 | Р на выходе P-6703A/B, сигн. H (блок.) | 3109-P-6703A/B outlet pressure Indicator Interlock Alarm | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6702 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,5 | MPaG | 0 | 1,5 | MPaG | 0,9 | 0,95 |  |  |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3109-PZT-67204/3109-S-JB-C437 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 7 | [12 empty] | Запись в БД произведена
1195 | 3109 | 3109 | 3109-XZV-67201 | SKLPD0021-00 | 3109-XZV-67201 |  |  | 3109-XZV-67201 | V-6702, блок. отсечки | 3109-V-6702 Interlock to cutt off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6702 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1196 | 3109 | 3109 | 3109-XZV-67201 | SKLPD0021-00 | 3109-XZV-67201 |  | 3109-Z-6702, 3109-Z-6791, 3000-Z-6295 | 3109-XZY-67201 | V-6702, блок. отсечки | 3109-V-6702 Interlock to cutt off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6702 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D444/3000-S-MC-B13 | PR04 | NH-KYJYP3 24x2.5 | 354 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D444 |  |  | 3109-XZY-67201/3109-S-JB-D444 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 11 | [12 empty] | Запись в БД произведена
1197 | 3109 | 3109 | 3109-XZV-67201 | SKLPD0021-00 | 3109-XZV-67201 |  |  | 3109-XZZSC-67201 | V-6702, блок. отсечки (закрыт) | 3109-V-6702 Interlock to cutt off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6702 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSC-67201/3109-S-JB-C439 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 6 | [12 empty] | Запись в БД произведена
1198 | 3109 | 3109 | 3109-XZV-67201 | SKLPD0021-00 | 3109-XZV-67201 |  |  | 3109-XZZSO-67201 | V-6702, блок. отсечки (открыт) | 3109-V-6702 Interlock to cutt off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6702 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSO-67201/3109-S-JB-C439 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 7 | [12 empty] | Запись в БД произведена
1200 | 3109 | 3109 | 3109-XZV-67203 | SKLPD0021-00 | 3109-XZV-67203 |  |  | 3109-XZV-67203 | P-6702, блок. отсечки выдачи | 3109-P-6702 Interlock to cut off the outfeed | On-Off Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6702 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1201 | 3109 | 3109 | 3109-XZV-67203 | SKLPD0021-00 | 3109-XZV-67203 |  | 3109-Z-6716, 3109-Z-6791 | 3109-XZY-67203 | P-6702, блок. отсечки выдачи | 3109-P-6702 Interlock to cut off the outfeed | Solenoid Valve | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6702 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR04 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3109-XZY-67203/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 0 | [12 empty] | Запись в БД произведена
1202 | 3109 | 3109 | 3109-XZV-67203 | SKLPD0021-00 | 3109-XZV-67203 |  |  | 3109-XZZSC-67203 | P-6702, блок. отсечки выдачи (закрыт) | 3109-P-6702 Interlock to cut off the outfeed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6702 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSC-67203/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 20 | [12 empty] | Запись в БД произведена
1203 | 3109 | 3109 | 3109-XZV-67203 | SKLPD0021-00 | 3109-XZV-67203 |  |  | 3109-XZZSO-67203 | P-6702, блок. отсечки выдачи (открыт) | 3109-P-6702 Interlock to cut off the outfeed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6702 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSO-67203/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 21 | [12 empty] | Запись в БД произведена
1205 | 3109 | Сombined Title | 3109-XZV-67204 | SKLPD0021-00 | 3109-XZV-67204 |  |  | 3109-XZV-67204 | P-6703A/B, блок. отсечки | 3109-P-6703A/B Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6702 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1206 | 3109 | Сombined Title | 3109-XZV-67204 | SKLPD0021-00 | 3109-XZV-67204 |  | 3109-Z-6716 | 3109-XZY-67204 | P-6703A/B, блок. отсечки | 3109-P-6703A/B Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6702 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D444/3000-S-MC-B13 | PR05 | NH-KYJYP3 24x2.5 | 354 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D444 |  |  | 3109-XZY-67204/3109-S-JB-D444 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 13 | [12 empty] | Запись в БД произведена
1207 | 3109 | Сombined Title | 3109-XZV-67204 | SKLPD0021-00 | 3109-XZV-67204 |  | 3102-Z-6202, 3102-Z-6207 | 3109-XZZSC-67204 | P-6703A/B, блок. отсечки (закрыт) | 3109-P-6703A/B Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6702 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSC-67204/3109-S-JB-C439 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 9 | [12 empty] | Запись в БД произведена
1208 | 3109 | Сombined Title | 3109-XZV-67204 | SKLPD0021-00 | 3109-XZV-67204 |  | 3102-Z-6202, 3102-Z-6207, 3104-Z-7202, 3104-Z-7207 | 3109-XZZSO-67204 | P-6703A/B, блок. отсечки (открыт) | 3109-P-6703A/B Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6702 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSO-67204/3109-S-JB-C439 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 10 | [12 empty] | Запись в БД произведена
1210 | 3109 | Сombined Title | 3109-XZV-67205 | SKLPD0021-00 | 3109-XZV-67205 |  |  | 3109-XZV-67205 | P-6703A/B, блок. отсечки выдачи | 3109-P-6703A/B Interlock to cut off the outfeed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6702 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1211 | 3109 |  | 3109-XZV-67205 | SKLPD0021-00 | 3109-XZV-67205 |  | 3109-Z-6716, 3109-Z-6791 | 3109-XZY-67205 | P-6703A/B, блок. отсечки выдачи | 3109-P-6703A/B Interlock to cut off the outfeed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6702 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR05 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3109-XZY-67205/3109-S-JB-D443 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 12 | [12 empty] | Запись в БД произведена
1212 | 3109 | Сombined Title | 3109-XZV-67205 | SKLPD0021-00 | 3109-XZV-67205 |  | 3102-Z-6202, 3102-Z-6207 | 3109-XZZSC-67205 | P-6703A/B, блок. отсечки выдачи (закрыт) | 3109-P-6703A/B Interlock to cut off the outfeed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6702 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSC-67205/3109-S-JB-C438 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 7 | [12 empty] | Запись в БД произведена
1213 | 3109 | Сombined Title | 3109-XZV-67205 | SKLPD0021-00 | 3109-XZV-67205 |  | 3102-Z-6202, 3102-Z-6207, 3104-Z-7202,3104-Z-7207 | 3109-XZZSO-67205 | P-6703A/B, блок. отсечки выдачи (открыт) | 3109-P-6703A/B Interlock to cut off the outfeed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-6702 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSO-67205/3109-S-JB-C438 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 8 | [12 empty] | Запись в БД произведена
1215 | 2202 | Сombined Title | 3109-MXI-06702A | SDO0001-01 | 3109-MXI-06702A |  | 3109-Z-6702, 3109-Z-6716, 3109-Z-6790 | 3109-MXI-06702A | SIS стоп насоса подачи EB 3109-P-6702 | EB Delivery Pump 3109-P-6702 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6702 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 8 | [12 empty] | Запись в БД произведена
1217 | 2202 | Сombined Title | 3109-MXI-06703A | SDO0001-01 | 3109-MXI-06703A |  | 3109-Z-6702, 3109-Z-6716, 3109-Z-6790, 3102-Z-6202, 3102-Z-6207, 3104-Z-7202, 3104-Z-7207 | 3109-MXI-06703A | SIS стоп авар. насоса EB 3109-P-6703A | Emergency EB Pump 3109-P-6703A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6702 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 9 | [12 empty] | Запись в БД произведена
1219 | 2202 | Сombined Title | 3109-MXI-16703A | SDO0001-01 | 3109-MXI-16703A |  | 3109-Z-6702, 3109-Z-6716, 3109-Z-6790, 3102-Z-6202, 3102-Z-6207, 3104-Z-7202, 3104-Z-7207 | 3109-MXI-16703A | SIS стоп авар. насоса EB 3109-P-6703B | Emergency EB Pump 3109-P-6703B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6702 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 18 | [12 empty] | Запись в БД произведена
1221 | 3109 | 3109 | 3109-LZIA-67302 | SAI1000-01R | 3109-LZIA-67302 |  | 3109-Z-6703 | 3109-LZT-67302 | Ур. в 3109-V-6703, сигн. HH (блок.) | 3109-V-6703 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6700 | mm | 0 | 100 | % | 6,865672 | 12,53731 | 86,26866 | 97,61194 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3109-LZT-67302/3109-S-JB-C437 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 13 | [12 empty] | Запись в БД произведена
1223 | 3109 | 3109 | 3109-XZV-67301 | SKLPD0021-00 | 3109-XZV-67301 |  |  | 3109-XZV-67301 | V-6703, блок. отсечки | 3109-V-6703 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1224 | 3109 | 3109 | 3109-XZV-67301 | SKLPD0021-00 | 3109-XZV-67301 |  | 3109-Z-6703, 3109-Z-6791 | 3109-XZY-67301 | V-6703, блок. отсечки | 3109-V-6703 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D444/3000-S-MC-B13 | PR06 | NH-KYJYP3 24x2.5 | 354 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D444 |  |  | 3109-XZY-67301/3109-S-JB-D444 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 15 | [12 empty] | Запись в БД произведена
1225 | 3109 | 3109 | 3109-XZV-67301 | SKLPD0021-00 | 3109-XZV-67301 |  |  | 3109-XZZSC-67301 | V-6703, блок. отсечки (закрыт) | 3109-V-6703 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3109-XZZSC-67301/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 22 | [12 empty] | Запись в БД произведена
1226 | 3109 | 3109 | 3109-XZV-67301 | SKLPD0021-00 | 3109-XZV-67301 |  |  | 3109-XZZSO-67301 | V-6703, блок. отсечки (открыт) | 3109-V-6703 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3109-XZZSO-67301/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 26 | [12 empty] | Запись в БД произведена
1228 | 3109 | 3109 | 3109-XZV-67302 | SKLPD0021-00 | 3109-XZV-67302 |  |  | 3109-XZV-67302 | P-6704/B, блок. отсечки | 3109-P-6704/B Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1229 | 3109 | 3109 | 3109-XZV-67302 | SKLPD0021-00 | 3109-XZV-67302 |  | 3109-Z-6719 | 3109-XZY-67302 | P-6704/B, блок. отсечки | 3109-P-6704/B Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D444/3000-S-MC-B13 | PR07 | NH-KYJYP3 24x2.5 | 354 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D444 |  |  | 3109-XZY-67302/3109-S-JB-D444 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 16 | [12 empty] | Запись в БД произведена
1230 | 3109 | 3109 | 3109-XZV-67302 | SKLPD0021-00 | 3109-XZV-67302 |  |  | 3109-XZZSC-67302 | P-6704/B, блок. отсечки (закрыт) | 3109-P-6704/B Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3109-XZZSC-67302/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 23 | [12 empty] | Запись в БД произведена
1231 | 3109 | 3109 | 3109-XZV-67302 | SKLPD0021-00 | 3109-XZV-67302 |  |  | 3109-XZZSO-67302 | P-6704/B, блок. отсечки (открыт) | 3109-P-6704/B Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3109-XZZSO-67302/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 27 | [12 empty] | Запись в БД произведена
1233 | 3109 | 3109 | 3109-XZV-67303 | SKLPD0021-00 | 3109-XZV-67303 |  |  | 3109-XZV-67303 | P-6703A/B, блок. отсечки выдачи | 3109-P-6703A/B Interlock to cut off the outfeed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1234 | 3109 | 3109 | 3109-XZV-67303 | SKLPD0021-00 | 3109-XZV-67303 |  | 3109-Z-6719, 3109-Z-6791 | 3109-XZY-67303 | P-6703A/B, блок. отсечки выдачи | 3109-P-6703A/B Interlock to cut off the outfeed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D445/3000-S-MC-B13 | PR02 | NH-KYJYP3 24x2.5 | 335 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D445 |  |  | 3109-XZY-67303/3109-S-JB-D445 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 20 | [12 empty] | Запись в БД произведена
1235 | 3109 | 3109 | 3109-XZV-67303 | SKLPD0021-00 | 3109-XZV-67303 |  |  | 3109-XZZSC-67303 | P-6703A/B, блок. отсечки выдачи (закрыт) | 3109-P-6703A/B Interlock to cut off the outfeed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3109-XZZSC-67303/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 11 | [12 empty] | Запись в БД произведена
1236 | 3109 | 3109 | 3109-XZV-67303 | SKLPD0021-00 | 3109-XZV-67303 |  |  | 3109-XZZSO-67303 | P-6703A/B, блок. отсечки выдачи (открыт) | 3109-P-6703A/B Interlock to cut off the outfeed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6703 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3109-XZZSO-67303/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 15 | [12 empty] | Запись в БД произведена
1238 | 2202 | 3109 | 3109-MXI-06704A | SDO0001-01 | 3109-MXI-06704A |  | 3109-Z-6703, 3109-Z-6719, 3109-Z-6790 | 3109-MXI-06704A | SIS стоп насоса подачи МО 3109-P-6704A | MO Delivery Pump 3109-P-6704A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6703 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 11 | [12 empty] | Запись в БД произведена
1239 | 2202 | 3109 | 3109-MXI-06703B | SDO0001-01 | 3109-MXI-06703B |  | #N/A | 3109-MXI-06703B | SIS пуск авар. насоса EB 3109-P-6703A | Emergency EB Pump 3109-P-6703A SIS Start Command | SIS Start Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6702 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 10 | [12 empty] | Запись в БД произведена
1241 | 2202 | 3109 | 3109-MXI-16704A | SDO0001-01 | 3109-MXI-16704A |  | 3109-Z-6703, 3109-Z-6719, 3109-Z-6790 | 3109-MXI-16704A | SIS стоп насоса подачи МО 3109-P-6704B | MO Delivery Pump 3109-P-6704B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6703 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 20 | [12 empty] | Запись в БД произведена
1242 | 2202 | 3109 | 3109-MXI-16703B | SDO0001-01 | 3109-MXI-16703B |  | #N/A | 3109-MXI-16703B | SIS пуск авар. насоса EB 3109-P-6703B | Emergency EB Pump 3109-P-6703B SIS Start Command | SIS Start Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6702 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 19 | [12 empty] | Запись в БД произведена
1244 | 3109 | 3109 | 3109-LZIA-67402 | SAI1000-01R | 3109-LZIA-67402 |  | 3109-Z-6704 | 3109-LZT-67402 | Ур. в 3109-V-6704, сигн. HH (блок.) | 3109-V-6704 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6500 | mm | 0 | 100 | % | 4,738462 | 7,076923 | 85,41538 | 97,10769 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3109-LZT-67402/3109-S-JB-C437 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 14 | [12 empty] | Запись в БД произведена
1246 | 3109 | 3109 | 3103-XZV-67401 | SKLPD0021-00 | 3103-XZV-67401 |  |  | 3103-XZV-67401 | V-6704, блок. отсечки | 3109-V-6704 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1247 | 3109 | 3109 | 3103-XZV-67401 | SKLPD0021-00 | 3103-XZV-67401 |  | 3109-Z-6704, 3109-Z-6791 | 3103-XZY-67401 | V-6704, блок. отсечки | 3109-V-6704 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR01 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3103-XZY-67401/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 1 | [12 empty] | Запись в БД произведена
1248 | 3109 | 3109 | 3103-XZV-67401 | SKLPD0021-00 | 3103-XZV-67401 |  |  | 3103-XZZSC-67401 | V-6704, блок. отсечки (закрыт) | 3109-V-6704 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3103-XZZSC-67401/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 22 | [12 empty] | Запись в БД произведена
1249 | 3109 | 3109 | 3103-XZV-67401 | SKLPD0021-00 | 3103-XZV-67401 |  |  | 3103-XZZSO-67401 | V-6704, блок. отсечки (открыт) | 3109-V-6704 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3103-XZZSO-67401/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 23 | [12 empty] | Запись в БД произведена
1251 | 3109 | 3109 | 3109-XZV-67402 | SKLPD0021-00 | 3109-XZV-67402 |  |  | 3109-XZV-67402 | P-6705A/B, блок. отсечки | 3109-P-6705A/B Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1252 | 3109 | 3109 | 3109-XZV-67402 | SKLPD0021-00 | 3109-XZV-67402 |  | 3109-Z-6720 | 3109-XZY-67402 | P-6705A/B, блок. отсечки | 3109-P-6705A/B Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR06 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3109-XZY-67402/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 4 | [12 empty] | Запись в БД произведена
1253 | 3109 | 3109 | 3109-XZV-67402 | SKLPD0021-00 | 3109-XZV-67402 |  |  | 3109-XZZSC-67402 | P-6705A/B, блок. отсечки (закрыт) | 3109-P-6705A/B Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSC-67402/3109-S-JB-C439 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 2 | [12 empty] | Запись в БД произведена
1254 | 3109 | 3109 | 3109-XZV-67402 | SKLPD0021-00 | 3109-XZV-67402 |  |  | 3109-XZZSO-67402 | P-6705A/B, блок. отсечки (открыт) | 3109-P-6705A/B Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C439/3000-S-MC-B05 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 354 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C439 |  |  | 3109-XZZSO-67402/3109-S-JB-C439 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 5 | [12 empty] | Запись в БД произведена
1256 | 3109 | 3109 | 3109-XZV-67403 | SKLPD0021-00 | 3109-XZV-67403 |  |  | 3109-XZV-67403 | P-6705A/B, блок. отсечки выдачи | 3109-P-6705A/B Interlock to cut off the outfeed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1257 | 3109 | 3109 | 3109-XZV-67403 | SKLPD0021-00 | 3109-XZV-67403 |  | 3109-Z-6720, 3109-Z-6791 | 3109-XZY-67403 | P-6705A/B, блок. отсечки выдачи | 3109-P-6705A/B Interlock to cut off the outfeed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR07 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3109-XZY-67403/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 5 | [12 empty] | Запись в БД произведена
1258 | 3109 | 3109 | 3109-XZV-67403 | SKLPD0021-00 | 3109-XZV-67403 |  |  | 3109-XZZSC-67403 | P-6705A/B, блок. отсечки выдачи (закрыт) | 3109-P-6705A/B Interlock to cut off the outfeed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C441/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C441 |  |  | 3109-XZZSC-67403/3109-S-JB-C441 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 23 | [12 empty] | Запись в БД произведена
1259 | 3109 | 3109 | 3109-XZV-67403 | SKLPD0021-00 | 3109-XZV-67403 |  |  | 3109-XZZSO-67403 | P-6705A/B, блок. отсечки выдачи (открыт) | 3109-P-6705A/B Interlock to cut off the outfeed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6704 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C441/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C441 |  |  | 3109-XZZSO-67403/3109-S-JB-C441 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 26 | [12 empty] | Запись в БД произведена
1261 | 2202 | 3109 | 3109-MXI-06705A | SDO0001-01 | 3109-MXI-06705A |  | 3109-Z-6704, 3109-Z-6720, 3109-Z-6790 | 3109-MXI-06705A | SIS стоп насоса подачи CM 3109-P-6705A | CM Delivery Pump 3109-P-6705A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6704 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 12 | [12 empty] | Запись в БД произведена
1263 | 2202 | 3109 | 3109-MXI-16705A | SDO0001-01 | 3109-MXI-16705A |  | 3109-Z-6704, 3109-Z-6720, 3109-Z-6790 | 3109-MXI-16705A | SIS стоп насоса подачи CM 3109-P-6705B | CM Delivery Pump 3109-P-6705B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6704 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 21 | [12 empty] | Запись в БД произведена
1265 | 3109 | 3109 | 3109-LZIA-67502 | SAI1000-01R | 3109-LZIA-67502 |  | 3109-Z-6705 | 3109-LZT-67502 | Ур. в 3109-V-6705, сигн. HH (блок.) | 3109-V-6705 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6500 | mm | 0 | 100 | % | 4,738462 | 7,076923 | 85,41538 | 97,10769 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3109-LZT-67502/3109-S-JB-C437 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 15 | [12 empty] | Запись в БД произведена
1267 | 3109 | 3109 | 3105-XZV-67501 | SKLPD0021-00 | 3105-XZV-67501 |  |  | 3105-XZV-67501 | V-6705, блок. отсечки | 3109-V-6705 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1268 | 3109 | 3109 | 3105-XZV-67501 | SKLPD0021-00 | 3105-XZV-67501 |  | 3109-Z-6705, 3109-Z-6791 | 3105-XZY-67501 | V-6705, блок. отсечки | 3109-V-6705 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR02 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3105-XZY-67501/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 2 | [12 empty] | Запись в БД произведена
1269 | 3109 | 3109 | 3105-XZV-67501 | SKLPD0021-00 | 3105-XZV-67501 |  |  | 3105-XZZSC-67501 | V-6705, блок. отсечки (закрыт) | 3109-V-6705 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3105-XZZSC-67501/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 24 | [12 empty] | Запись в БД произведена
1270 | 3109 | 3109 | 3105-XZV-67501 | SKLPD0021-00 | 3105-XZV-67501 |  |  | 3105-XZZSO-67501 | V-6705, блок. отсечки (открыт) | 3109-V-6705 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3105-XZZSO-67501/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 25 | [12 empty] | Запись в БД произведена
1272 | 3109 | 3109 | 3109-XZV-67502 | SKLPD0021-00 | 3109-XZV-67502 |  |  | 3109-XZV-67502 | P-6706A/B, блок. отсечки | 3109-P-6706A/B Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1273 | 3109 | 3109 | 3109-XZV-67502 | SKLPD0021-00 | 3109-XZV-67502 |  | 3109-Z-6721 | 3109-XZY-67502 | P-6706A/B, блок. отсечки | 3109-P-6706A/B Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR08 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3109-XZY-67502/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 6 | [12 empty] | Запись в БД произведена
1274 | 3109 | 3109 | 3109-XZV-67502 | SKLPD0021-00 | 3109-XZV-67502 |  |  | 3109-XZZSC-67502 | P-6706A/B, блок. отсечки (закрыт) | 3109-P-6706A/B Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C441/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C441 |  |  | 3109-XZZSC-67502/3109-S-JB-C441 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 24 | [12 empty] | Запись в БД произведена
1275 | 3109 | 3109 | 3109-XZV-67502 | SKLPD0021-00 | 3109-XZV-67502 |  |  | 3109-XZZSO-67502 | P-6706A/B, блок. отсечки (открыт) | 3109-P-6706A/B Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C441/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C441 |  |  | 3109-XZZSO-67502/3109-S-JB-C441 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 27 | [12 empty] | Запись в БД произведена
1277 | 3109 | 3109 | 3109-XZV-67503 | SKLPD0021-00 | 3109-XZV-67503 |  |  | 3109-XZV-67503 | P-6706A/B, блок. отсечки выдачи | 3109-P-6706A/B Interlock to cut off the outfeed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1278 | 3109 | 3109 | 3109-XZV-67503 | SKLPD0021-00 | 3109-XZV-67503 |  | 3109-Z-6721, 3109-Z-6791 | 3109-XZY-67503 | P-6706A/B, блок. отсечки выдачи | 3109-P-6706A/B Interlock to cut off the outfeed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR09 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3109-XZY-67503/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 7 | [12 empty] | Запись в БД произведена
1279 | 3109 | 3109 | 3109-XZV-67503 | SKLPD0021-00 | 3109-XZV-67503 |  |  | 3109-XZZSC-67503 | P-6706A/B, блок. отсечки выдачи (закрыт) | 3109-P-6706A/B Interlock to cut off the outfeed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSC-67503/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 26 | [12 empty] | Запись в БД произведена
1280 | 3109 | 3109 | 3109-XZV-67503 | SKLPD0021-00 | 3109-XZV-67503 |  |  | 3109-XZZSO-67503 | P-6706A/B, блок. отсечки выдачи (открыт) | 3109-P-6706A/B Interlock to cut off the outfeed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6705 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSO-67503/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 29 | [12 empty] | Запись в БД произведена
1282 | 2202 | 3109 | 3109-MXI-06706A | SDO0001-01 | 3109-MXI-06706A |  | 3109-Z-6705, 3109-Z-6721, 3109-Z-6790 | 3109-MXI-06706A | SIS стоп насоса подачи CM 3109-P-6706A | CM Delivery Pump 3109-P-6706A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6705 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 13 | [12 empty] | Запись в БД произведена
1284 | 2202 | 3109 | 3109-MXI-16706A | SDO0001-01 | 3109-MXI-16706A |  | 3109-Z-6705, 3109-Z-6721, 3109-Z-6790 | 3109-MXI-16706A | SIS стоп насоса подачи CM 3109-P-6706B | CM Delivery Pump 3109-P-6706B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6705 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 22 | [12 empty] | Запись в БД произведена
1286 | 3109 | 3109 | 3109-LZIA-67602 | SAI1000-01R | 3109-LZIA-67602 |  | 3109-Z-6706 | 3109-LZT-67602 | Ур. в 3109-V-6706, сигн. HH (блок.) | 3109-V-6706 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 5100 | mm | 0 | 100 | % | 3,529412 | 5,882353 | 84,70588 | 96,47059 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3109-LZT-67602/3109-S-JB-C437 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 12 | [12 empty] | Запись в БД произведена
1288 | 3109 | 3109 | 3103-XZV-67601 | SKLPD0021-00 | 3103-XZV-67601 |  |  | 3103-XZV-67601 | V-6706, блок. отсечки | 3109-V-6706 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1289 | 3109 | 3109 | 3103-XZV-67601 | SKLPD0021-00 | 3103-XZV-67601 |  | 3109-Z-6706, 3109-Z-6791 | 3103-XZY-67601 | V-6706, блок. отсечки | 3109-V-6706 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D444/3000-S-MC-B13 | PR01 | NH-KYJYP3 24x2.5 | 354 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D444 |  |  | 3103-XZY-67601/3109-S-JB-D444 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 12 | [12 empty] | Запись в БД произведена
1290 | 3109 | 3109 | 3103-XZV-67601 | SKLPD0021-00 | 3103-XZV-67601 |  |  | 3103-XZZSC-67601 | V-6706, блок. отсечки (закрыт) | 3109-V-6706 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3103-XZZSC-67601/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 20 | [12 empty] | Запись в БД произведена
1291 | 3109 | 3109 | 3103-XZV-67601 | SKLPD0021-00 | 3103-XZV-67601 |  |  | 3103-XZZSO-67601 | V-6706, блок. отсечки (открыт) | 3109-V-6706 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3103-XZZSO-67601/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 21 | [12 empty] | Запись в БД произведена
1293 | 3109 | 3109 | 3109-XZV-67602 | SKLPD0021-00 | 3109-XZV-67602 |  |  | 3109-XZV-67602 | P-6707, блок. отсечки | 3109-P-6707 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1294 | 3109 | 3109 | 3109-XZV-67602 | SKLPD0021-00 | 3109-XZV-67602 |  | 3109-Z-6722 | 3109-XZY-67602 | P-6707, блок. отсечки | 3109-P-6707 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D445/3000-S-MC-B13 | PR03 | NH-KYJYP3 24x2.5 | 335 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D445 |  |  | 3109-XZY-67602/3109-S-JB-D445 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 21 | [12 empty] | Запись в БД произведена
1295 | 3109 | 3109 | 3109-XZV-67602 | SKLPD0021-00 | 3109-XZV-67602 |  |  | 3109-XZZSC-67602 | P-6707, блок. отсечки (закрыт) | 3109-P-6707 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3109-XZZSC-67602/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 12 | [12 empty] | Запись в БД произведена
1296 | 3109 | 3109 | 3109-XZV-67602 | SKLPD0021-00 | 3109-XZV-67602 |  |  | 3109-XZZSO-67602 | P-6707, блок. отсечки (открыт) | 3109-P-6707 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3109-XZZSO-67602/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 16 | [12 empty] | Запись в БД произведена
1298 | 3109 | 3109 | 3109-XZV-67603 | SKLPD0021-00 | 3109-XZV-67603 |  |  | 3109-XZV-67603 | P-6707, блок. отсечки выдачи | 3109-P-6707 Interlock to cut off the outfeed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1299 | 3109 | 3109 | 3109-XZV-67603 | SKLPD0021-00 | 3109-XZV-67603 |  | 3109-Z-6722, 3109-Z-6791 | 3109-XZY-67603 | P-6707, блок. отсечки выдачи | 3109-P-6707 Interlock to cut off the outfeed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR10 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3109-XZY-67603/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 8 | [12 empty] | Запись в БД произведена
1300 | 3109 | 3109 | 3109-XZV-67603 | SKLPD0021-00 | 3109-XZV-67603 |  |  | 3109-XZZSC-67603 | P-6707, блок. отсечки выдачи (закрыт) | 3109-P-6707 Interlock to cut off the outfeed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSC-67603/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 27 | [12 empty] | Запись в БД произведена
1301 | 3109 | 3109 | 3109-XZV-67603 | SKLPD0021-00 | 3109-XZV-67603 |  |  | 3109-XZZSO-67603 | P-6707, блок. отсечки выдачи (открыт) | 3109-P-6707 Interlock to cut off the outfeed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR13 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSO-67603/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 30 | [12 empty] | Запись в БД произведена
1303 | 3109 | 3109 | 3109-TZIA-66364 | SAI1000-01R | 3109-TZIA-66364 |  | 3109-Z-6722 | 3109-TZT-66364 | Т подшипника 3109-P-6707 | 3109-P-6707 Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6706 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3109-TZT-66364/3000-S-MC-B01 |  | NH-IA-DJYYP3 1x2x1.5 | 341 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B01 | Одиночный |  | 3109-TZT-66364/3000-S-MC-B01 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 11 | [12 empty] | Запись в БД произведена
1304 | 2202 | 3109 | 3109-MXI-06707A | SDO0001-01 | 3109-MXI-06707A |  | 3109-Z-6706, 3109-Z-6722, 3109-Z-6790 | 3109-MXI-06707A | SIS стоп насоса подачи легких компонентов 3109-P-6707 | Light Component Delivery Pump 3109-P-6707 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6706 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 14 | [12 empty] | Запись в БД произведена
1306 | 3109 | 3109 | 3109-LZIA-67702 | SAI1000-01R | 3109-LZIA-67702 |  | 3109-Z-6707 | 3109-LZT-67702 | Ур. в 3109-V-6707, сигн. HH (блок.) | 3109-V-6707 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 5100 | mm | 0 | 100 | % | 5,882353 | 11,76471 | 84,70588 | 96,47059 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3109-LZT-67702/3109-S-JB-C437 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 13 | [12 empty] | Запись в БД произведена
1308 | 3109 | 3109 | 3103-XZV-67701 | SKLPD0021-00 | 3103-XZV-67701 |  |  | 3103-XZV-67701 | V-6707, блок. отсечки | 3109-V-6707 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1309 | 3109 | 3109 | 3103-XZV-67701 | SKLPD0021-00 | 3103-XZV-67701 |  | 3109-Z-6707, 3109-Z-6791 | 3103-XZY-67701 | V-6707, блок. отсечки | 3109-V-6707 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D445/3000-S-MC-B13 | PR01 | NH-KYJYP3 24x2.5 | 335 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D445 |  |  | 3103-XZY-67701/3109-S-JB-D445 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 19 | [12 empty] | Запись в БД произведена
1310 | 3109 | 3109 | 3103-XZV-67701 | SKLPD0021-00 | 3103-XZV-67701 |  |  | 3103-XZZSC-67701 | V-6707, блок. отсечки (закрыт) | 3109-V-6707 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3103-XZZSC-67701/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 9 | [12 empty] | Запись в БД произведена
1311 | 3109 | 3109 | 3103-XZV-67701 | SKLPD0021-00 | 3103-XZV-67701 |  |  | 3103-XZZSO-67701 | V-6707, блок. отсечки (открыт) | 3109-V-6707 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3103-XZZSO-67701/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 10 | [12 empty] | Запись в БД произведена
1313 | 3109 | 3109 | 3109-XZV-67702 | SKLPD0021-00 | 3109-XZV-67702 |  |  | 3109-XZV-67702 | P-6708, блок. отсечки | 3109-P-6708 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1314 | 3109 | 3109 | 3109-XZV-67702 | SKLPD0021-00 | 3109-XZV-67702 |  | 3109-Z-6724 | 3109-XZY-67702 | P-6708, блок. отсечки | 3109-P-6708 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D445/3000-S-MC-B13 | PR04 | NH-KYJYP3 24x2.5 | 335 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D445 |  |  | 3109-XZY-67702/3109-S-JB-D445 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 22 | [12 empty] | Запись в БД произведена
1315 | 3109 | 3109 | 3109-XZV-67702 | SKLPD0021-00 | 3109-XZV-67702 |  |  | 3109-XZZSC-67702 | P-6708, блок. отсечки (закрыт) | 3109-P-6708 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3109-XZZSC-67702/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 13 | [12 empty] | Запись в БД произведена
1316 | 3109 | 3109 | 3109-XZV-67702 | SKLPD0021-00 | 3109-XZV-67702 |  |  | 3109-XZZSO-67702 | P-6708, блок. отсечки (открыт) | 3109-P-6708 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3109-XZZSO-67702/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 17 | [12 empty] | Запись в БД произведена
1318 | 3109 | 3109 | 3109-XZV-67703 | SKLPD0021-00 | 3109-XZV-67703 |  |  | 3109-XZV-67703 | P-6708, блок. отсечки выдачи | 3109-P-6708 Interlock to cut off the outfeed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1319 | 3109 | 3109 | 3109-XZV-67703 | SKLPD0021-00 | 3109-XZV-67703 |  | 3109-Z-6724, 3109-Z-6791 | 3109-XZY-67703 | P-6708, блок. отсечки выдачи | 3109-P-6708 Interlock to cut off the outfeed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR11 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3109-XZY-67703/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 9 | [12 empty] | Запись в БД произведена
1320 | 3109 | 3109 | 3109-XZV-67703 | SKLPD0021-00 | 3109-XZV-67703 |  |  | 3109-XZZSC-67703 | P-6708, блок. отсечки выдачи (закрыт) | 3109-P-6708 Interlock to cut off the outfeed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSC-67703/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 28 | [12 empty] | Запись в БД произведена
1321 | 3109 | 3109 | 3109-XZV-67703 | SKLPD0021-00 | 3109-XZV-67703 |  |  | 3109-XZZSO-67703 | P-6708, блок. отсечки выдачи (открыт) | 3109-P-6708 Interlock to cut off the outfeed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6707 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C438/3000-S-MC-B05 | PR14 | NH-IA-DJYP3YP3 16x2x1.0 | 335 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C438 |  |  | 3109-XZZSO-67703/3109-S-JB-C438 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 31 | [12 empty] | Запись в БД произведена
1323 | 2202 | 3109 | 3109-MXI-06708A | SDO0001-01 | 3109-MXI-06708A |  | 3109-Z-6707, 3109-Z-6724, 3109-Z-6790 | 3109-MXI-06708A | SIS стоп насоса подачи олигомеров 3109-P-6708 | Oligomer Delivery Pump 3109-P-6708 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6707 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 15 | [12 empty] | Запись в БД произведена
1325 | 3109 | 3109 | 3109-LZIA-67802 | SAI1000-01R | 3109-LZIA-67802 |  | 3109-Z-6708 | 3109-LZT-67802 | Ур. в 3109-V-6713, сигн. HH (блок.) | 3109-V-6713 Liquid level indication HH interlock alarm | D/P Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6500 | mm | 0 | 100 | % | 7,076923 | 12,92308 | 85,41538 | 97,10769 |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3109-LZT-67802/3109-S-JB-C437 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 14 | [12 empty] | Запись в БД произведена
1327 | 3109 | 3109 | 3109-XZV-67801 | SKLPD0021-00 | 3109-XZV-67801 |  |  | 3109-XZV-67801 | V-6713, блок. отсечки | 3109-V-6713 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1328 | 3109 | 3109 | 3109-XZV-67801 | SKLPD0021-00 | 3109-XZV-67801 |  | 3109-Z-6708, 3109-Z-6791 | 3109-XZY-67801 | V-6713, блок. отсечки | 3109-V-6713 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D444/3000-S-MC-B13 | PR08 | NH-KYJYP3 24x2.5 | 354 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D444 |  |  | 3109-XZY-67801/3109-S-JB-D444 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 17 | [12 empty] | Запись в БД произведена
1329 | 3109 | 3109 | 3109-XZV-67801 | SKLPD0021-00 | 3109-XZV-67801 |  |  | 3109-XZZSC-67801 | V-6713, блок. отсечки (закрыт) | 3109-V-6713 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3109-XZZSC-67801/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 24 | [12 empty] | Запись в БД произведена
1330 | 3109 | 3109 | 3109-XZV-67801 | SKLPD0021-00 | 3109-XZV-67801 |  |  | 3109-XZZSO-67801 | V-6713, блок. отсечки (открыт) | 3109-V-6713 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3109-XZZSO-67801/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 28 | [12 empty] | Запись в БД произведена
1332 | 3109 | 3109 | 3109-XZV-67802 | SKLPD0021-00 | 3109-XZV-67802 |  |  | 3109-XZV-67802 | P-6713A/B, блок. отсечки | 3109-P-6713A/B Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1333 | 3109 | 3109 | 3109-XZV-67802 | SKLPD0021-00 | 3109-XZV-67802 |  | 3109-Z-6726 | 3109-XZY-67802 | P-6713A/B, блок. отсечки | 3109-P-6713A/B Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D444/3000-S-MC-B13 | PR09 | NH-KYJYP3 24x2.5 | 354 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D444 |  |  | 3109-XZY-67802/3109-S-JB-D444 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 18 | [12 empty] | Запись в БД произведена
1334 | 3109 | 3109 | 3109-XZV-67802 | SKLPD0021-00 | 3109-XZV-67802 |  |  | 3109-XZZSC-67802 | P-6713A/B, блок. отсечки (закрыт) | 3109-P-6713A/B Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3109-XZZSC-67802/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 25 | [12 empty] | Запись в БД произведена
1335 | 3109 | 3109 | 3109-XZV-67802 | SKLPD0021-00 | 3109-XZV-67802 |  |  | 3109-XZZSO-67802 | P-6713A/B, блок. отсечки (открыт) | 3109-P-6713A/B Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C442/3000-S-MC-B05 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C442 |  |  | 3109-XZZSO-67802/3109-S-JB-C442 | 3000-S-SC-B03 | 3000-S-MC-B06 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 29 | [12 empty] | Запись в БД произведена
1337 | 3109 | 3109 | 3109-XZV-67803 | SKLPD0021-00 | 3109-XZV-67803 |  |  | 3109-XZV-67803 | P-6713A/B, блок. отсечки выдачи | 3109-P-6713A/B Interlock to cut off the outfeed | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1338 | 3109 | 3109 | 3109-XZV-67803 | SKLPD0021-00 | 3109-XZV-67803 |  | 3109-Z-6726, 3109-Z-6791 | 3109-XZY-67803 | P-6713A/B, блок. отсечки выдачи | 3109-P-6713A/B Interlock to cut off the outfeed | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D445/3000-S-MC-B13 | PR05 | NH-KYJYP3 24x2.5 | 335 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D445 |  |  | 3109-XZY-67803/3109-S-JB-D445 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 23 | [12 empty] | Запись в БД произведена
1339 | 3109 | 3109 | 3109-XZV-67803 | SKLPD0021-00 | 3109-XZV-67803 |  |  | 3109-XZZSC-67803 | P-6713A/B, блок. отсечки выдачи (закрыт) | 3109-P-6713A/B Interlock to cut off the outfeed | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3109-XZZSC-67803/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 14 | [12 empty] | Запись в БД произведена
1340 | 3109 | 3109 | 3109-XZV-67803 | SKLPD0021-00 | 3109-XZV-67803 |  |  | 3109-XZZSO-67803 | P-6713A/B, блок. отсечки выдачи (открыт) | 3109-P-6713A/B Interlock to cut off the outfeed | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6708 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3109-XZZSO-67803/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 18 | [12 empty] | Запись в БД произведена
1342 | 2202 | 3109 | 3109-MXI-06713A | SDO0001-01 | 3109-MXI-06713A |  | 3109-Z-6708, 3109-Z-6726, 3109-Z-6790 | 3109-MXI-06713A | SIS стоп насоса подачи спец. МО 3109-P-6713A | Special MO Delivery Pump 3109-P-6713A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6708 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 16 | [12 empty] | Запись в БД произведена
1344 | 2202 | 3109 | 3109-MXI-16713A | SDO0001-01 | 3109-MXI-16713A |  | 3109-Z-6708, 3109-Z-6726, 3109-Z-6790 | 3109-MXI-16713A | SIS стоп насоса подачи спец. МО 3109-P-6713B | Special MO Delivery Pump 3109-P-6713B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6708 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 23 | [12 empty] | Запись в БД произведена
1346 | 3104 | Сombined Title | 3104-FZIA-72004 | SAI1000-01R | 3104-FZIA-72004 |  | 3104-Z-7201 | 3104-FZT-72004 | Рег. расхода от 3104-MX-7201 к 3104-E-7201 | 3104-MX-7201 to 3104-E-7201 flow control | CORIOLIS FLOW TRANSMITTER | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | AIR-EP | Exd | SIS | I | 24V DC 4-wire external Power | 20 | 0 | 30000 | kg/h | 0 | 30000 | kg/h | 4000 | 4500 |  |  |  | kg/h |  | 24V external power supply |  | ИД 2026 07 03 |  |  |  | 3104-FZT-72004/3000-S-MC-B04 |  | NH-DJYYP3 1x2x1.5 | 386 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B04 | Одиночный |  | 3104-FZT-72004/3000-S-MC-B04 | 3000-S-SC-B01 | 3000-S-MC-B04 |  | A11 | A12 | 04 | - | A11-04 | - | A12-04 | - | 9 | [12 empty] | Запись в БД произведена
1348 | 3104 | Сombined Title | 3104-TZIA-72003 | SAI1000-01R | 3104-TZIA-72003 |  | 3104-Z-7201 | 3104-TZT-72003 | Т на выходе трубного пучка 3104-E-7201 | 3104-E-7201's tube-side outlet temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 150 | ℃ | -50 | 150 | ℃ |  |  | 90 | 95 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C312/3000-S-MC-B03 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C312 |  |  | 3104-TZT-72003/3104-S-JB-C312 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 0 | [12 empty] | Запись в БД произведена
1350 | 3104 | Сombined Title | 3104-XZV-72001 | SKLPD0021-00 | 3104-XZV-72001 |  |  | 3104-XZV-72001 | Вход 3104-MX-7201, блок. отсечки | 3104-MX-7201 inlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1351 | 3104 | Сombined Title | 3104-XZV-72001 | SKLPD0021-00 | 3104-XZV-72001 |  | 3104-Z-7201, 3104-Z-7291 | 3104-XZY-72001 | Вход 3104-MX-7201, блок. отсечки | 3104-MX-7201 inlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR03 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3104-XZY-72001/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 15 | [12 empty] | Запись в БД произведена
1352 | 3104 | Сombined Title | 3104-XZV-72001 | SKLPD0021-00 | 3104-XZV-72001 |  |  | 3104-XZZSC-72001 | Вход 3104-MX-7201, блок. отсечки (закрыт) | 3104-MX-7201 inlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3104-XZZSC-72001/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 14 | [12 empty] | Запись в БД произведена
1353 | 3104 | Сombined Title | 3104-XZV-72001 | SKLPD0021-00 | 3104-XZV-72001 |  |  | 3104-XZZSO-72001 | Вход 3104-MX-7201, блок. отсечки (открыт) | 3104-MX-7201 inlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3104-XZZSO-72001/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 19 | [12 empty] | Запись в БД произведена
1355 | 3104 | Сombined Title | 3104-XZV-72002 | SKLPD0021-00 | 3104-XZV-72002 |  |  | 3104-XZV-72002 | EB к 3104-MX-7201, блок. отсечки | EB to 3104-MX-7201 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1356 | 3104 | Сombined Title | 3104-XZV-72002 | SKLPD0021-00 | 3104-XZV-72002 |  | 3104-Z-7203, 3104-Z-7204, 3104-Z-7291 | 3104-XZY-72002 | EB к 3104-MX-7201, блок. отсечки | EB to 3104-MX-7201 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR09 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3104-XZY-72002/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 16 | [12 empty] | Запись в БД произведена
1357 | 3104 | Сombined Title | 3104-XZV-72002 | SKLPD0021-00 | 3104-XZV-72002 |  |  | 3104-XZZSC-72002 | EB к 3104-MX-7201, блок. отсечки (закрыт) | EB to 3104-MX-7201 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C301/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C301 |  |  | 3104-XZZSC-72002/3104-S-JB-C301 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 2 | [12 empty] | Запись в БД произведена
1358 | 3104 | Сombined Title | 3104-XZV-72002 | SKLPD0021-00 | 3104-XZV-72002 |  |  | 3104-XZZSO-72002 | EB к 3104-MX-7201, блок. отсечки (открыт) | EB to 3104-MX-7201 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C301/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C301 |  |  | 3104-XZZSO-72002/3104-S-JB-C301 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 4 | [12 empty] | Запись в БД произведена
1360 | 3104 | Сombined Title | 3101-XZV-72003 | SKLPD0021-00 | 3101-XZV-72003 |  |  | 3101-XZV-72003 | Инициатор к 3104-MX-7202, блок. отсечки | initator to 3104-MX-7202 Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1361 | 3104 | Сombined Title | 3101-XZV-72003 | SKLPD0021-00 | 3101-XZV-72003 |  | 3104-Z-7201, 3104-Z-7291 | 3101-XZY-72003 | Инициатор к 3104-MX-7202, блок. отсечки | initator to 3104-MX-7202 Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D313/3000-S-MC-B11 | PR01 | NH-KYJYP3 16x2.5 | 410 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D313 |  |  | 3101-XZY-72003/3104-S-JB-D313 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 24 | [12 empty] | Запись в БД произведена
1362 | 3104 | Сombined Title | 3101-XZV-72003 | SKLPD0021-00 | 3101-XZV-72003 |  |  | 3101-XZZSC-72003 | Инициатор к 3104-MX-7202, блок. отсечки (закрыт) | initator to 3104-MX-7202 Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3101-XZZSC-72003/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 16 | [12 empty] | Запись в БД произведена
1363 | 3104 | Сombined Title | 3101-XZV-72003 | SKLPD0021-00 | 3101-XZV-72003 |  |  | 3101-XZZSO-72003 | Инициатор к 3104-MX-7202, блок. отсечки (открыт) | initator to 3104-MX-7202 Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3101-XZZSO-72003/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 17 | [12 empty] | Запись в БД произведена
1365 | 3104 | Сombined Title | 3109-XZV-72022 | SKLPD0021-00 | 3109-XZV-72022 |  |  | 3109-XZV-72022 | Отс. клап. цирк. р-ра к 3104-MX-7201 | Circulating solution to 3104-MX-7201 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1366 | 3104 | Сombined Title | 3109-XZV-72022 | SKLPD0021-00 | 3109-XZV-72022 |  | 3104-Z-7201 | 3109-XZY-72022 | Отс. клап. цирк. р-ра к 3104-MX-7201 | Circulating solution to 3104-MX-7201 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR02 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3109-XZY-72022/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 23 | [12 empty] | Запись в БД произведена
1367 | 3104 | Сombined Title | 3109-XZV-72022 | SKLPD0021-00 | 3109-XZV-72022 |  |  | 3109-XZZSC-72022 | Отс. клап. цирк. р-ра к 3104-MX-7201 (закрыт) | Circulating solution to 3104-MX-7201 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C301/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C301 |  |  | 3109-XZZSC-72022/3104-S-JB-C301 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 6 | [12 empty] | Запись в БД произведена
1368 | 3104 | Сombined Title | 3109-XZV-72022 | SKLPD0021-00 | 3109-XZV-72022 |  |  | 3109-XZZSO-72022 | Отс. клап. цирк. р-ра к 3104-MX-7201 (открыт) | Circulating solution to 3104-MX-7201 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C301/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C301 |  |  | 3109-XZZSO-72022/3104-S-JB-C301 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 7 | [12 empty] | Запись в БД произведена
1370 | 3104 | Сombined Title | 3101-XZV-72023 | SKLPD0021-00 | 3101-XZV-72023 |  |  | 3101-XZV-72023 | Отс. клап. стирола от 3101-F-6101A/B к 3104-MX-7201 | 3101-F-6101A/B's styrene to 3104-MX-7201 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1371 | 3104 | Сombined Title | 3101-XZV-72023 | SKLPD0021-00 | 3101-XZV-72023 |  | 3104-Z-7201, 3104-Z-7291 | 3101-XZY-72023 | Отс. клап. стирола от 3101-F-6101A/B к 3104-MX-7201 | 3101-F-6101A/B's styrene to 3104-MX-7201 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR01 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3101-XZY-72023/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 14 | [12 empty] | Запись в БД произведена
1372 | 3104 | Сombined Title | 3101-XZV-72023 | SKLPD0021-00 | 3101-XZV-72023 |  |  | 3101-XZZSC-72023 | Отс. клап. стирола от F-6101A/B к MX-7201 (закрыт) | 3101-F-6101A/B's styrene to 3104-MX-7201 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C301/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C301 |  |  | 3101-XZZSC-72023/3104-S-JB-C301 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 0 | [12 empty] | Запись в БД произведена
1373 | 3104 | Сombined Title | 3101-XZV-72023 | SKLPD0021-00 | 3101-XZV-72023 |  |  | 3101-XZZSO-72023 | Отс. клап. стирола от F-6101A/B к MX-7201 (открыт) | 3101-F-6101A/B's styrene to 3104-MX-7201 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C301/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C301 |  |  | 3101-XZZSO-72023/3104-S-JB-C301 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 1 | [12 empty] | Запись в БД произведена
1375 | 3104 | Сombined Title | 3104-PZIA-72005A | SAI1000-01R | 3104-PZIA-72005A |  | 3104-Z-7204 | 3104-PZT-72005A | Р на выходе 3104-EJ-7202 | 3104-EJ-7202 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C296/3000-S-MC-B02 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C296 |  |  | 3104-PZT-72005A/3104-S-JB-C296 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 6 | [12 empty] | Запись в БД произведена
1376 | 3104 | Сombined Title | 3104-PZIA-72005B | SAI1000-01R | 3104-PZIA-72005B |  | 3104-Z-7204 | 3104-PZT-72005B | Р на выходе 3104-EJ-7202 | 3104-EJ-7202 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C309/3000-S-MC-B02 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C309 |  |  | 3104-PZT-72005B/3104-S-JB-C309 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 9 | [12 empty] | Запись в БД произведена
1377 | 3104 | Сombined Title | 3104-PZIA-72005C | SAI1000-01R | 3104-PZIA-72005C |  | 3104-Z-7204 | 3104-PZT-72005C | Р на выходе 3104-EJ-7202 | 3104-EJ-7202 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C312/3000-S-MC-B03 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C312 |  |  | 3104-PZT-72005C/3104-S-JB-C312 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 2 | [12 empty] | Запись в БД произведена
1379 | 3104 | Сombined Title | 3104-TZIA-72005A | SAI1000-01R | 3104-TZIA-72005A |  | 3104-Z-7202, 3104-Z-7203 | 3104-TZT-72005A | Т 3104-R-7201 | 3104-R-7201 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-TZT-72005A/3104-S-JB-C249 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 8 | [12 empty] | Запись в БД произведена
1380 | 3104 | Сombined Title | 3104-TZIA-72005B | SAI1000-01R | 3104-TZIA-72005B |  | 3104-Z-7202, 3104-Z-7203 | 3104-TZT-72005B | Т 3104-R-7201 | 3104-R-7201 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-TZT-72005B/3104-S-JB-C261 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 6 | [12 empty] | Запись в БД произведена
1381 | 3104 | Сombined Title | 3104-TZIA-72005C | SAI1000-01R | 3104-TZIA-72005C |  | 3104-Z-7202, 3104-Z-7203 | 3104-TZT-72005C | Т 3104-R-7201 | 3104-R-7201 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C262/3000-S-MC-B03 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C262 |  |  | 3104-TZT-72005C/3104-S-JB-C262 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 3 | [12 empty] | Запись в БД произведена
1383 | 3104 | Сombined Title | 3104-LZSA-72031A | SDI0010-01R | 3104-LZSA-72031A |  | 3104-Z-7222 | 3104-LZS-72031A | Ур. на входе 3104-P-7202A | 3104-P-7202A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C272/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C272 |  |  | 3104-LZS-72031A/3104-S-JB-C272 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 11 | [12 empty] | Запись в БД произведена
1385 | 3104 | Сombined Title | 3104-LZSA-72031B | SDI0010-01R | 3104-LZSA-72031B |  | 3104-Z-7222 | 3104-LZS-72031B | Ур. на входе 3104-P-7202B | 3104-P-7202B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3104-LZS-72031B/3104-S-JB-C274 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 24 | [12 empty] | Запись в БД произведена
1387 | 3104 | Сombined Title | 3104-XZV-72004 | SKLPD0021-00 | 3104-XZV-72004 |  |  | 3104-XZV-72004 | Промывка EB | EB rinse | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1388 | 3104 | Сombined Title | 3104-XZV-72004 | SKLPD0021-00 | 3104-XZV-72004 |  | 3104-Z-7204 | 3104-XZY-72004 | Промывка EB | EB rinse | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D313/3000-S-MC-B11 | PR02 | NH-KYJYP3 16x2.5 | 410 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D313 |  |  | 3104-XZY-72004/3104-S-JB-D313 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 25 | [12 empty] | Запись в БД произведена
1389 | 3104 | Сombined Title | 3104-XZV-72004 | SKLPD0021-00 | 3104-XZV-72004 |  |  | 3104-XZZSC-72004 | Промывка EB (закрыт) | EB rinse | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3104-XZZSC-72004/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 18 | [12 empty] | Запись в БД произведена
1390 | 3104 | Сombined Title | 3104-XZV-72004 | SKLPD0021-00 | 3104-XZV-72004 |  |  | 3104-XZZSO-72004 | Промывка EB (открыт) | EB rinse | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3104-XZZSO-72004/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 22 | [12 empty] | Запись в БД произведена
1392 | 3104 | Сombined Title | 3104-XZV-72006 | SKLPD0021-00 | 3104-XZV-72006 |  |  | 3104-XZV-72006 | Азот к отх. газу, блок. отсечки | Nitrogen to off gas Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1393 | 3104 | Сombined Title | 3104-XZV-72006 | SKLPD0021-00 | 3104-XZV-72006 |  | 3104-Z-7204 | 3104-XZY-72006 | Азот к отх. газу, блок. отсечки | Nitrogen to off gas Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D320/3000-S-MC-B11 | PR01 | NH-KYJYP3 16x2.5 | 396 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D320 |  |  | 3104-XZY-72006/3104-S-JB-D320 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 0 | [12 empty] | Запись в БД произведена
1394 | 3104 | Сombined Title | 3104-XZV-72006 | SKLPD0021-00 | 3104-XZV-72006 |  |  | 3104-XZZSC-72006 | Азот к отх. газу, блок. отсечки (закрыт) | Nitrogen to off gas Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3104-XZZSC-72006/3104-S-JB-C306 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 28 | [12 empty] | Запись в БД произведена
1395 | 3104 | Сombined Title | 3104-XZV-72006 | SKLPD0021-00 | 3104-XZV-72006 |  |  | 3104-XZZSO-72006 | Азот к отх. газу, блок. отсечки (открыт) | Nitrogen to off gas Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3104-XZZSO-72006/3104-S-JB-C306 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 24 | [12 empty] | Запись в БД произведена
1397 | 3104 | Сombined Title | 3104-XZV-72007 | SKLPD0021-00 | 3104-XZV-72007 |  |  | 3104-XZV-72007 | Выход 3104-EJ-7201, блок. отсечки | 3104-EJ-7201 outlet Interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1398 | 3104 | Сombined Title | 3104-XZV-72007 | SKLPD0021-00 | 3104-XZV-72007 |  | 3104-Z-7204, 3104-Z-7291 | 3104-XZY-72007 | Выход 3104-EJ-7201, блок. отсечки | 3104-EJ-7201 outlet Interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D320/3000-S-MC-B11 | PR02 | NH-KYJYP3 16x2.5 | 396 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D320 |  |  | 3104-XZY-72007/3104-S-JB-D320 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 1 | [12 empty] | Запись в БД произведена
1399 | 3104 | Сombined Title | 3104-XZV-72007 | SKLPD0021-00 | 3104-XZV-72007 |  |  | 3104-XZZSC-72007 | Выход 3104-EJ-7201, блок. отсечки (закрыт) | 3104-EJ-7201 outlet Interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3104-XZZSC-72007/3104-S-JB-C306 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 29 | [12 empty] | Запись в БД произведена
1400 | 3104 | Сombined Title | 3104-XZV-72007 | SKLPD0021-00 | 3104-XZV-72007 |  |  | 3104-XZZSO-72007 | Выход 3104-EJ-7201, блок. отсечки (открыт) | 3104-EJ-7201 outlet Interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3104-XZZSO-72007/3104-S-JB-C306 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 25 | [12 empty] | Запись в БД произведена
1402 | 3104 | Сombined Title | 3104-XZV-72101 | SKLPD0021-00 | 3104-XZV-72101 |  |  | 3104-XZV-72101 | Вход 3104-P-7202AB | 3104-P-7202AB Inlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1403 | 3104 | Сombined Title | 3104-XZV-72101 | SKLPD0021-00 | 3104-XZV-72101 |  | 3104-Z-7247 | 3104-XZY-72101 | Вход 3104-P-7202AB | 3104-P-7202AB Inlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR06 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3104-XZY-72101/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 20 | [12 empty] | Запись в БД произведена
1404 | 3104 | Сombined Title | 3104-XZV-72101 | SKLPD0021-00 | 3104-XZV-72101 |  |  | 3104-XZZSC-72101 | Вход 3104-P-7202AB (закрыт) | 3104-P-7202AB Inlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3104-XZZSC-72101/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 17 | [12 empty] | Запись в БД произведена
1406 | 3104 | Сombined Title | 3104-XZV-72102 | SKLPD0021-00 | 3104-XZV-72102 |  |  | 3104-XZV-72102 | Выход 3104-P-7202AB | 3104-P-7202AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1407 | 3104 | Сombined Title | 3104-XZV-72102 | SKLPD0021-00 | 3104-XZV-72102 |  | 3104-Z-7247 | 3104-XZY-72102 | Выход 3104-P-7202AB | 3104-P-7202AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D286/3000-S-MC-B14 | PR08 | NH-KYJYP3 24x2.5 | 378 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D286 |  |  | 3104-XZY-72102/3104-S-JB-D286 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 23 | [12 empty] | Запись в БД произведена
1408 | 3104 | Сombined Title | 3104-XZV-72102 | SKLPD0021-00 | 3104-XZV-72102 |  |  | 3104-XZZSC-72102 | Выход 3104-P-7202AB (закрыт) | 3104-P-7202AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C282/3000-S-MC-B08 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 378 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C282 |  |  | 3104-XZZSC-72102/3104-S-JB-C282 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 1 | [12 empty] | Запись в БД произведена
1410 | 3104 | Сombined Title | 3104-XZV-72021 | SKLPD0021-00 | 3104-XZV-72021 |  |  | 3104-XZV-72021 | Масл. дренаж к 3105-V-7208, блок. отсечки | Oily drain to 3105-V-7208 interlock to cut offf | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1411 | 3104 | Сombined Title | 3104-XZV-72021 | SKLPD0021-00 | 3104-XZV-72021 |  | 3104-Z-7291 | 3104-XZY-72021 | Масл. дренаж к 3105-V-7208, блок. отсечки | Oily drain to 3105-V-7208 interlock to cut offf | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR04 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3104-XZY-72021/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 17 | [12 empty] | Запись в БД произведена
1412 | 3104 | Сombined Title | 3104-XZV-72021 | SKLPD0021-00 | 3104-XZV-72021 |  |  | 3104-XZZSC-72021 | Масл. дренаж к 3105-V-7208, блок. отсечки (закрыт) | Oily drain to 3105-V-7208 interlock to cut offf | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3104-XZZSC-72021/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 15 | [12 empty] | Запись в БД произведена
1413 | 3104 | Сombined Title | 3104-XZV-72021 | SKLPD0021-00 | 3104-XZV-72021 |  |  | 3104-XZZSO-72021 | Масл. дренаж к 3105-V-7208, блок. отсечки (открыт) | Oily drain to 3105-V-7208 interlock to cut offf | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3104-XZZSO-72021/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 20 | [12 empty] | Запись в БД произведена
1415 | 3104 | Сombined Title | 3104-XZV-72027 | SKLPD0021-00 | 3104-XZV-72027 |  |  | 3104-XZV-72027 | Отс. клап. на выходе 3109-P-6703 | 3109-P-6703 outlet cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1416 | 3104 | Сombined Title | 3104-XZV-72027 | SKLPD0021-00 | 3104-XZV-72027 |  | 3104-Z-7204, 3104-Z-7203, 3104-Z-7291 | 3104-XZY-72027 | Отс. клап. на выходе 3109-P-6703 | 3109-P-6703 outlet cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR05 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3104-XZY-72027/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 18 | [12 empty] | Запись в БД произведена
1417 | 3104 | Сombined Title | 3104-XZV-72027 | SKLPD0021-00 | 3104-XZV-72027 |  |  | 3104-XZZSC-72027 | Отс. клап. на выходе 3109-P-6703 (закрыт) | 3109-P-6703 outlet cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3104-XZZSC-72027/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 16 | [12 empty] | Запись в БД произведена
1418 | 3104 | Сombined Title | 3104-XZV-72027 | SKLPD0021-00 | 3104-XZV-72027 |  |  | 3104-XZZSO-72027 | Отс. клап. на выходе 3109-P-6703 (открыт) | 3109-P-6703 outlet cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3104-XZZSO-72027/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 21 | [12 empty] | Запись в БД произведена
1420 | 3104 | Сombined Title | 3104-XZV-72028 | SKLPD0021-00 | 3104-XZV-72028 |  |  | 3104-XZV-72028 | Отс. клап. EB на входе 3104-R-7202 | 3104-R-7202's EB cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1421 | 3104 | Сombined Title | 3104-XZV-72028 | SKLPD0021-00 | 3104-XZV-72028 |  | Z-7209, 3104-Z-7208, 3104-Z-7209, 3104-Z-7291 | 3104-XZY-72028 | Отс. клап. EB на входе 3104-R-7202 | 3104-R-7202's EB cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D313/3000-S-MC-B11 | PR05 | NH-KYJYP3 16x2.5 | 410 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D313 |  |  | 3104-XZY-72028/3104-S-JB-D313 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 28 | [12 empty] | Запись в БД произведена
1422 | 3104 | Сombined Title | 3104-XZV-72028 | SKLPD0021-00 | 3104-XZV-72028 |  |  | 3104-XZZSC-72028 | Отс. клап. EB на входе 3104-R-7202 (закрыт) | 3104-R-7202's EB cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3104-XZZSC-72028/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 21 | [12 empty] | Запись в БД произведена
1423 | 3104 | Сombined Title | 3104-XZV-72028 | SKLPD0021-00 | 3104-XZV-72028 |  |  | 3104-XZZSO-72028 | Отс. клап. EB на входе 3104-R-7202 (открыт) | 3104-R-7202's EB cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3104-XZZSO-72028/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 25 | [12 empty] | Запись в БД произведена
1425 | 3104 | Сombined Title | 3104-TZIA-66352A | SAI1000-01R | 3104-TZIA-66352A |  | 3104-Z-7247 | 3104-TZT-66352A | Т подшипника 3104-P-7202A | 3104-P-7202A Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-TZT-66352A/3104-S-JB-C249 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 7 | [12 empty] | Запись в БД произведена
1426 | 2202 | Сombined Title | 3104-MXI-07202A | SDO0001-01 | 3104-MXI-07202A |  | 3104-Z-7222, 3104-Z-7247, Z-7290H, 3104-Z-7290 | 3104-MXI-07202A | SIS стоп насоса рецикла первого преполим. 3104-P-7202A | First Pre-Polymerizer Reflux Pump 3104-P-7202A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7202 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 7 | [12 empty] | Запись в БД произведена
1428 | 3104 | Сombined Title | 3104-TZIA-66352B | SAI1000-01R | 3104-TZIA-66352B |  | 3104-Z-7247 | 3104-TZT-66352B | Т подшипника 3104-P-7202B | 3104-P-7202B Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7202 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-TZT-66352B/3104-S-JB-C261 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 14 | [12 empty] | Запись в БД произведена
1429 | 2202 | Сombined Title | 3104-MXI-17202A | SDO0001-01 | 3104-MXI-17202A |  | 3104-Z-7222, 3104-Z-7247, Z-7290H, 3104-Z-7290 | 3104-MXI-17202A | SIS стоп насоса рецикла первого преполим. 3104-P-7202B | First Pre-Polymerizer Reflux Pump 3104-P-7202B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7202 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 14 | [12 empty] | Запись в БД произведена
1431 | 3104 | Сombined Title | 3104-PZIA-72007A | SAI1000-01R | 3104-PZIA-72007A |  | 3104-Z-7205 | 3104-PZT-72007A | Р нагнетания 3104-P-7201B | 3104-P-7201B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-PZT-72007A/3104-S-JB-C249 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 9 | [12 empty] | Запись в БД произведена
1432 | 3104 | Сombined Title | 3104-PZIA-72007B | SAI1000-01R | 3104-PZIA-72007B |  | 3104-Z-7205 | 3104-PZT-72007B | Р нагнетания 3104-P-7201B | 3104-P-7201B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-PZT-72007B/3104-S-JB-C261 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 7 | [12 empty] | Запись в БД произведена
1433 | 3104 | Сombined Title | 3104-PZIA-72007C | SAI1000-01R | 3104-PZIA-72007C |  | 3104-Z-7205 | 3104-PZT-72007C | Р нагнетания 3104-P-7201B | 3104-P-7201B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C262/3000-S-MC-B03 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C262 |  |  | 3104-PZT-72007C/3104-S-JB-C262 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 4 | [12 empty] | Запись в БД произведена
1435 | 3104 | Сombined Title | 3104-PZIA-72008A | SAI1000-01R | 3104-PZIA-72008A |  | 3104-Z-7206 | 3104-PZT-72008A | Р нагнетания 3104-P-7201A | 3104-P-7201A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-PZT-72008A/3104-S-JB-C249 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 10 | [12 empty] | Запись в БД произведена
1436 | 3104 | Сombined Title | 3104-PZIA-72008B | SAI1000-01R | 3104-PZIA-72008B |  | 3104-Z-7206 | 3104-PZT-72008B | Р нагнетания 3104-P-7201A | 3104-P-7201A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-PZT-72008B/3104-S-JB-C261 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 8 | [12 empty] | Запись в БД произведена
1437 | 3104 | Сombined Title | 3104-PZIA-72008C | SAI1000-01R | 3104-PZIA-72008C |  | 3104-Z-7206 | 3104-PZT-72008C | Р нагнетания 3104-P-7201A | 3104-P-7201A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7203 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,1 | 1,25 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C262/3000-S-MC-B03 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C262 |  |  | 3104-PZT-72008C/3104-S-JB-C262 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 5 | [12 empty] | Запись в БД произведена
1439 | 2202 | 3104 | 3104-MXI-77201A | SDO0001-01 | 3104-MXI-77201A |  | 3104-Z-7290 | 3104-MXI-77201A | SIS стоп мешалки первого преполим. 3104-AG-7201 | First Pre-Polymerizer Agitator 3104-AG-7201 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7203 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 20 | [12 empty] | Запись в БД произведена
1441 | 2202 | Сombined Title | 3104-MXI-07201A | SDO0001-01 | 3104-MXI-07201A |  | 3104-Z-7205, 3104-Z-7290 | 3104-MXI-07201A | SIS стоп расплавного насоса первого преполим. 3104-P-7201A | First Pre-Polymerizer Melt Pump 3104-P-7201A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7203 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 6 | [12 empty] | Запись в БД произведена
1442 | 2202 | 3104 | 3104-MII-07201 | SAI1000-01R | 3104-MII-07201 |  | 3104-Z-7205 | 3104-MII-07201 | Ток расплавного насоса первого преполим. 3104-P-7201A | First Pre-Polymerizer Melt Pump 3104-P-7201A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7203 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 14 | [12 empty] | Запись в БД произведена
1444 | 2202 | Сombined Title | 3104-MXI-17201A | SDO0001-01 | 3104-MXI-17201A |  | 3104-Z-7206, 3104-Z-7290 | 3104-MXI-17201A | SIS стоп расплавного насоса первого преполим. 3104-P-7201B | First Pre-Polymerizer Melt Pump 3104-P-7201B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7203 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 13 | [12 empty] | Запись в БД произведена
1445 | 2202 | 3104 | 3104-MII-17201 | SAI1000-01R | 3104-MII-17201 |  | 3104-Z-7206 | 3104-MII-17201 | Ток расплавного насоса первого преполим. 3104-P-7201B | First Pre-Polymerizer Melt Pump 3104-P-7201B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7203 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 04 | - | A72-04 | - | A73-04 | - | 15 | [12 empty] | Запись в БД произведена
1447 | 3104 | Сombined Title | 3104-PZIA-72009A | SAI1000-01R | 3104-PZIA-72009A |  | 3104-Z-7209 | 3104-PZT-72009A | Р на выходе 3104-EJ-7204 | 3104-EJ-7204 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C296/3000-S-MC-B02 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C296 |  |  | 3104-PZT-72009A/3104-S-JB-C296 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 5 | [12 empty] | Запись в БД произведена
1448 | 3104 | Сombined Title | 3104-PZIA-72009B | SAI1000-01R | 3104-PZIA-72009B |  | 3104-Z-7209 | 3104-PZT-72009B | Р на выходе 3104-EJ-7204 | 3104-EJ-7204 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C309/3000-S-MC-B02 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C309 |  |  | 3104-PZT-72009B/3104-S-JB-C309 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 8 | [12 empty] | Запись в БД произведена
1449 | 3104 | Сombined Title | 3104-PZIA-72009C | SAI1000-01R | 3104-PZIA-72009C |  | 3104-Z-7209 | 3104-PZT-72009C | Р на выходе 3104-EJ-7204 | 3104-EJ-7204 outlet pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 500 | kPaA | 0 | 500 | kPaA |  |  | 150 | 400 |  | kPaA |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C312/3000-S-MC-B03 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C312 |  |  | 3104-PZT-72009C/3104-S-JB-C312 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 1 | [12 empty] | Запись в БД произведена
1451 | 3104 | Сombined Title | 3104-TZIA-72011A | SAI1000-01R | 3104-TZIA-72011A |  | 3104-Z-7207, 3104-Z-7208, Z-7208H | 3104-TZT-72011A | Т 3104-R-7202 | 3104-R-7202 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-TZT-72011A/3104-S-JB-C249 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 11 | [12 empty] | Запись в БД произведена
1452 | 3104 | Сombined Title | 3104-TZIA-72011B | SAI1000-01R | 3104-TZIA-72011B |  | 3104-Z-7207, 3104-Z-7208, Z-7208H | 3104-TZT-72011B | Т 3104-R-7202 | 3104-R-7202 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-TZT-72011B/3104-S-JB-C261 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 9 | [12 empty] | Запись в БД произведена
1453 | 3104 | Сombined Title | 3104-TZIA-72011C | SAI1000-01R | 3104-TZIA-72011C |  | 3104-Z-7207, 3104-Z-7208, Z-7208H | 3104-TZT-72011C | Т 3104-R-7202 | 3104-R-7202 temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 210 | ℃ | -50 | 210 | ℃ |  |  | 155 | 170 | Rate of temperature rise≥5℃/min | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C262/3000-S-MC-B03 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C262 |  |  | 3104-TZT-72011C/3104-S-JB-C262 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 6 | [12 empty] | Запись в БД произведена
1455 | 3104 | Сombined Title | 3104-LZSA-72032A | SDI0010-01R | 3104-LZSA-72032A |  | 3104-Z-7223 | 3104-LZS-72032A | Ур. на входе 3104-P-7204A | 3104-P-7204A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C254/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 427 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C254 |  |  | 3104-LZS-72032A/3104-S-JB-C254 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 9 | [12 empty] | Запись в БД произведена
1457 | 3104 | Сombined Title | 3104-LZSA-72032B | SDI0010-01R | 3104-LZSA-72032B |  | 3104-Z-7223 | 3104-LZS-72032B | Ур. на входе 3104-P-7204B | 3104-P-7204B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C255/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C255 |  |  | 3104-LZS-72032B/3104-S-JB-C255 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 10 | [12 empty] | Запись в БД произведена
1459 | 3104 | Сombined Title | 3104-XZV-72008 | SKLPD0021-00 | 3104-XZV-72008 |  |  | 3104-XZV-72008 | P-7201A/B к R-7202, блок. отсечки | 3104-P-7201A/B to 3104-R-7202 interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1460 | 3104 | Сombined Title | 3104-XZV-72008 | SKLPD0021-00 | 3104-XZV-72008 |  | 3104-Z-7204, 3104-Z-7209, Z-7209H | 3104-XZY-72008 | P-7201A/B к R-7202, блок. отсечки | 3104-P-7201A/B to 3104-R-7202 interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR01 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3104-XZY-72008/3104-S-JB-D263 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 13 | [12 empty] | Запись в БД произведена
1461 | 3104 | Сombined Title | 3104-XZV-72008 | SKLPD0021-00 | 3104-XZV-72008 |  |  | 3104-XZZSC-72008 | P-7201A/B к R-7202, блок. отсечки (закрыт) | 3104-P-7201A/B to 3104-R-7202 interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C272/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C272 |  |  | 3104-XZZSC-72008/3104-S-JB-C272 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 12 | [12 empty] | Запись в БД произведена
1462 | 3104 | Сombined Title | 3104-XZV-72008 | SKLPD0021-00 | 3104-XZV-72008 |  |  | 3104-XZZSO-72008 | P-7201A/B к R-7202, блок. отсечки (открыт) | 3104-P-7201A/B to 3104-R-7202 interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C272/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C272 |  |  | 3104-XZZSO-72008/3104-S-JB-C272 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 14 | [12 empty] | Запись в БД произведена
1464 | 3104 | Сombined Title | 3104-XZV-72009 | SKLPD0021-00 | 3104-XZV-72009 |  |  | 3104-XZV-72009 | Промывка EB | EB rinse | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1465 | 3104 | Сombined Title | 3104-XZV-72009 | SKLPD0021-00 | 3104-XZV-72009 |  | 3104-Z-7209 | 3104-XZY-72009 | Промывка EB | EB rinse | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D313/3000-S-MC-B11 | PR03 | NH-KYJYP3 16x2.5 | 410 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D313 |  |  | 3104-XZY-72009/3104-S-JB-D313 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 26 | [12 empty] | Запись в БД произведена
1466 | 3104 | Сombined Title | 3104-XZV-72009 | SKLPD0021-00 | 3104-XZV-72009 |  |  | 3104-XZZSC-72009 | Промывка EB (закрыт) | EB rinse | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3104-XZZSC-72009/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 19 | [12 empty] | Запись в БД произведена
1467 | 3104 | Сombined Title | 3104-XZV-72009 | SKLPD0021-00 | 3104-XZV-72009 |  |  | 3104-XZZSO-72009 | Промывка EB (открыт) | EB rinse | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3104-XZZSO-72009/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 23 | [12 empty] | Запись в БД произведена
1469 | 3104 | Сombined Title | 3104-XZV-72010 | SKLPD0021-00 | 3104-XZV-72010 |  |  | 3104-XZV-72010 | EB к R-7202, блок. отсечки | EB to 3104-R-7202 interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1470 | 3104 | Сombined Title | 3104-XZV-72010 | SKLPD0021-00 | 3104-XZV-72010 |  | 3104-Z-7208, 3104-Z-7209, 3104-Z-7291 | 3104-XZY-72010 | EB к R-7202, блок. отсечки | EB to 3104-R-7202 interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D313/3000-S-MC-B11 | PR04 | NH-KYJYP3 16x2.5 | 410 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D313 |  |  | 3104-XZY-72010/3104-S-JB-D313 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 27 | [12 empty] | Запись в БД произведена
1471 | 3104 | Сombined Title | 3104-XZV-72010 | SKLPD0021-00 | 3104-XZV-72010 |  |  | 3104-XZZSC-72010 | EB к R-7202, блок. отсечки (закрыт) | EB to 3104-R-7202 interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3104-XZZSC-72010/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 20 | [12 empty] | Запись в БД произведена
1472 | 3104 | Сombined Title | 3104-XZV-72010 | SKLPD0021-00 | 3104-XZV-72010 |  |  | 3104-XZZSO-72010 | EB к R-7202, блок. отсечки (открыт) | EB to 3104-R-7202 interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C315/3000-S-MC-B09 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C315 |  |  | 3104-XZZSO-72010/3104-S-JB-C315 | 3000-S-SC-B01 | 3000-S-MC-B09 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 24 | [12 empty] | Запись в БД произведена
1474 | 3104 | Сombined Title | 3104-XZV-72011 | SKLPD0021-00 | 3104-XZV-72011 |  |  | 3104-XZV-72011 | Азот к отх. газу, блок. отсечки | Nitrogen to off gas interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1475 | 3104 | Сombined Title | 3104-XZV-72011 | SKLPD0021-00 | 3104-XZV-72011 |  | 3104-Z-7209 | 3104-XZY-72011 | Азот к отх. газу, блок. отсечки | Nitrogen to off gas interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D320/3000-S-MC-B11 | PR03 | NH-KYJYP3 16x2.5 | 396 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D320 |  |  | 3104-XZY-72011/3104-S-JB-D320 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 2 | [12 empty] | Запись в БД произведена
1476 | 3104 | Сombined Title | 3104-XZV-72011 | SKLPD0021-00 | 3104-XZV-72011 |  |  | 3104-XZZSC-72011 | Азот к отх. газу, блок. отсечки (закрыт) | Nitrogen to off gas interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3104-XZZSC-72011/3104-S-JB-C306 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 30 | [12 empty] | Запись в БД произведена
1477 | 3104 | Сombined Title | 3104-XZV-72011 | SKLPD0021-00 | 3104-XZV-72011 |  |  | 3104-XZZSO-72011 | Азот к отх. газу, блок. отсечки (открыт) | Nitrogen to off gas interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3104-XZZSO-72011/3104-S-JB-C306 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 26 | [12 empty] | Запись в БД произведена
1479 | 3104 | Сombined Title | 3104-XZV-72012 | SKLPD0021-00 | 3104-XZV-72012 |  |  | 3104-XZV-72012 | Выход 3104-EJ-7203, блок. отсечки | 3104-EJ-7203 outlet interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1480 | 3104 | Сombined Title | 3104-XZV-72012 | SKLPD0021-00 | 3104-XZV-72012 |  | 3104-Z-7209, 3104-Z-7291 | 3104-XZY-72012 | Выход 3104-EJ-7203, блок. отсечки | 3104-EJ-7203 outlet interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D320/3000-S-MC-B11 | PR04 | NH-KYJYP3 16x2.5 | 396 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D320 |  |  | 3104-XZY-72012/3104-S-JB-D320 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 3 | [12 empty] | Запись в БД произведена
1481 | 3104 | Сombined Title | 3104-XZV-72012 | SKLPD0021-00 | 3104-XZV-72012 |  |  | 3104-XZZSC-72012 | Выход 3104-EJ-7203, блок. отсечки (закрыт) | 3104-EJ-7203 outlet interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3104-XZZSC-72012/3104-S-JB-C306 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 31 | [12 empty] | Запись в БД произведена
1482 | 3104 | Сombined Title | 3104-XZV-72012 | SKLPD0021-00 | 3104-XZV-72012 |  |  | 3104-XZZSO-72012 | Выход 3104-EJ-7203, блок. отсечки (открыт) | 3104-EJ-7203 outlet interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3104-XZZSO-72012/3104-S-JB-C306 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 27 | [12 empty] | Запись в БД произведена
1484 | 3104 | Сombined Title | 3104-XZV-72015 | SKLPD0021-00 | 3104-XZV-72015 |  |  | 3104-XZV-72015 | Поток 3104-MX-7205, отсечка подачи | 3104-MX-7205 stream cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1485 | 3104 | Сombined Title | 3104-XZV-72015 | SKLPD0021-00 | 3104-XZV-72015 |  | 3104-Z-7209, 3104-Z-7291 | 3104-XZY-72015 | Поток 3104-MX-7205, отсечка подачи | 3104-MX-7205 stream cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D286/3000-S-MC-B14 | PR07 | NH-KYJYP3 24x2.5 | 378 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D286 |  |  | 3104-XZY-72015/3104-S-JB-D286 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 22 | [12 empty] | Запись в БД произведена
1486 | 3104 | Сombined Title | 3104-XZV-72015 | SKLPD0021-00 | 3104-XZV-72015 |  |  | 3104-XZZSC-72015 | Поток 3104-MX-7205, отсечка подачи (закрыт) | 3104-MX-7205 stream cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C282/3000-S-MC-B08 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 378 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C282 |  |  | 3104-XZZSC-72015/3104-S-JB-C282 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 0 | [12 empty] | Запись в БД произведена
1487 | 3104 | Сombined Title | 3104-XZV-72015 | SKLPD0021-00 | 3104-XZV-72015 |  |  | 3104-XZZSO-72015 | Поток 3104-MX-7205, отсечка подачи (открыт) | 3104-MX-7205 stream cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C282/3000-S-MC-B08 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 378 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C282 |  |  | 3104-XZZSO-72015/3104-S-JB-C282 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 2 | [12 empty] | Запись в БД произведена
1489 | 3104 | Сombined Title | 3104-XZV-72103 | SKLPD0021-00 | 3104-XZV-72103 |  |  | 3104-XZV-72103 | Вход 3104-P-7204AB | 3104-P-7204AB Inlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1490 | 3104 | Сombined Title | 3104-XZV-72103 | SKLPD0021-00 | 3104-XZV-72103 |  | 3104-Z-7248 | 3104-XZY-72103 | Вход 3104-P-7204AB | 3104-P-7204AB Inlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR07 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3104-XZY-72103/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 21 | [12 empty] | Запись в БД произведена
1491 | 3104 | Сombined Title | 3104-XZV-72103 | SKLPD0021-00 | 3104-XZV-72103 |  |  | 3104-XZZSC-72103 | Вход 3104-P-7204AB (закрыт) | 3104-P-7204AB Inlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3104-XZZSC-72103/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 18 | [12 empty] | Запись в БД произведена
1493 | 3104 | Сombined Title | 3104-XZV-72104 | SKLPD0021-00 | 3104-XZV-72104 |  |  | 3104-XZV-72104 | Выход 3104-P-7204AB | 3104-P-7204AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1494 | 3104 | Сombined Title | 3104-XZV-72104 | SKLPD0021-00 | 3104-XZV-72104 |  | 3104-Z-7248 | 3104-XZY-72104 | Выход 3104-P-7204AB | 3104-P-7204AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR02 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3104-XZY-72104/3104-S-JB-D263 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 14 | [12 empty] | Запись в БД произведена
1495 | 3104 | Сombined Title | 3104-XZV-72104 | SKLPD0021-00 | 3104-XZV-72104 |  |  | 3104-XZZSC-72104 | Выход 3104-P-7204AB (закрыт) | 3104-P-7204AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C272/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C272 |  |  | 3104-XZZSC-72104/3104-S-JB-C272 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 13 | [12 empty] | Запись в БД произведена
1497 | 3104 | Сombined Title | 3104-TZIA-66354A | SAI1000-01R | 3104-TZIA-66354A |  | 3104-Z-7248 | 3104-TZT-66354A | Т подшипника 3104-P-7204A | 3104-P-7204A Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-TZT-66354A/3000-S-MC-B02 |  | NH-IA-DJYYP3 1x2x1.5 | 411 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B02 | Одиночный |  | 3104-TZT-66354A/3000-S-MC-B02 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 11 | [12 empty] | Запись в БД произведена
1498 | 2202 | Сombined Title | 3104-MXI-07204A | SDO0001-01 | 3104-MXI-07204A |  | 3104-Z-7223, 3104-Z-7248, Z-7290H, 3104-Z-7290 | 3104-MXI-07204A | SIS стоп насоса рецикла второго преполим. 3104-P-7204A | Second Pre-Polymerizer Reflux Pump 3104-P-7204A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7204 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 9 | [12 empty] | Запись в БД произведена
1500 | 3104 | Сombined Title | 3104-TZIA-66354B | SAI1000-01R | 3104-TZIA-66354B |  | 3104-Z-7248 | 3104-TZT-66354B | Т подшипника 3104-P-7204B | 3104-P-7204B Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7204 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3104-TZT-66354B/3000-S-MC-B02 |  | NH-IA-DJYYP3 1x2x1.5 | 411 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B02 | Одиночный |  | 3104-TZT-66354B/3000-S-MC-B02 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 12 | [12 empty] | Запись в БД произведена
1501 | 2202 | Сombined Title | 3104-MXI-17204A | SDO0001-01 | 3104-MXI-17204A |  | 3104-Z-7223, 3104-Z-7248, Z-7290H, 3104-Z-7290 | 3104-MXI-17204A | SIS стоп насоса рецикла второго преполим. 3104-P-7204B | Second Pre-Polymerizer Reflux Pump 3104-P-7204B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7204 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 16 | [12 empty] | Запись в БД произведена
1503 | 3104 | Сombined Title | 3104-PZIA-72011A | SAI1000-01R | 3104-PZIA-72011A |  | 3104-Z-7210, 3104-Z-7211 | 3104-PZT-72011A | Р нагнетания 3104-P-7203A/B | 3104-P-7203A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,55 | 1,7 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-PZT-72011A/3104-S-JB-C249 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 00 | - | A11-00 | - | A12-00 | - | 12 | [12 empty] | Запись в БД произведена
1504 | 3104 | Сombined Title | 3104-PZIA-72011B | SAI1000-01R | 3104-PZIA-72011B |  | 3104-Z-7210, 3104-Z-7211 | 3104-PZT-72011B | Р нагнетания 3104-P-7203A/B | 3104-P-7203A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,55 | 1,7 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-PZT-72011B/3104-S-JB-C261 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 01 | - | A11-01 | - | A12-01 | - | 10 | [12 empty] | Запись в БД произведена
1505 | 3104 | Сombined Title | 3104-PZIA-72011C | SAI1000-01R | 3104-PZIA-72011C |  | 3104-Z-7210, 3104-Z-7211 | 3104-PZT-72011C | Р нагнетания 3104-P-7203A/B | 3104-P-7203A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,55 | 1,7 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C262/3000-S-MC-B03 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C262 |  |  | 3104-PZT-72011C/3104-S-JB-C262 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 7 | [12 empty] | Запись в БД произведена
1507 | 3104 | Сombined Title | 3104-XZV-72013 | SKLPD0021-00 | 3104-XZV-72013 |  |  | 3104-XZV-72013 | Поток 3104-MX-7203, отсечка подачи | 3104-MX-7203's stream cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1508 | 3104 | Сombined Title | 3104-XZV-72013 | SKLPD0021-00 | 3104-XZV-72013 |  | 3104-Z-7209, 3104-Z-7291 | 3104-XZY-72013 | Поток 3104-MX-7203, отсечка подачи | 3104-MX-7203's stream cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D286/3000-S-MC-B14 | PR02 | NH-KYJYP3 24x2.5 | 378 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D286 |  |  | 3104-XZY-72013/3104-S-JB-D286 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 21 | [12 empty] | Запись в БД произведена
1509 | 3104 | Сombined Title | 3104-XZV-72013 | SKLPD0021-00 | 3104-XZV-72013 |  |  | 3104-XZZSC-72013 | Поток 3104-MX-7203, отсечка подачи (закрыт) | 3104-MX-7203's stream cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3104-XZZSC-72013/3104-S-JB-C288 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 30 | [12 empty] | Запись в БД произведена
1510 | 3104 | Сombined Title | 3104-XZV-72013 | SKLPD0021-00 | 3104-XZV-72013 |  |  | 3104-XZZSO-72013 | Поток 3104-MX-7203, отсечка подачи (открыт) | 3104-MX-7203's stream cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3104-XZZSO-72013/3104-S-JB-C288 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 31 | [12 empty] | Запись в БД произведена
1512 | 3104 | Сombined Title | 3104-XZV-72014 | SKLPD0021-00 | 3104-XZV-72014 |  |  | 3104-XZV-72014 | P-7203A/B к MX-7203, блок. отсечки | 3104-P-7203A/B to 3104-MX-7203 interlock to cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1513 | 3104 | Сombined Title | 3104-XZV-72014 | SKLPD0021-00 | 3104-XZV-72014 |  | 3104-Z-7209, Z-7291H, 3104-Z-7291 | 3104-XZY-72014 | P-7203A/B к MX-7203, блок. отсечки | 3104-P-7203A/B to 3104-MX-7203 interlock to cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR03 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3104-XZY-72014/3104-S-JB-D264 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 19 | [12 empty] | Запись в БД произведена
1514 | 3104 | Сombined Title | 3104-XZV-72014 | SKLPD0021-00 | 3104-XZV-72014 |  |  | 3104-XZZSC-72014 | P-7203A/B к MX-7203, блок. отсечки (закрыт) | 3104-P-7203A/B to 3104-MX-7203 interlock to cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3104-XZZSC-72014/3104-S-JB-C274 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 25 | [12 empty] | Запись в БД произведена
1515 | 3104 | Сombined Title | 3104-XZV-72014 | SKLPD0021-00 | 3104-XZV-72014 |  |  | 3104-XZZSO-72014 | P-7203A/B к MX-7203, блок. отсечки (открыт) | 3104-P-7203A/B to 3104-MX-7203 interlock to cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3104-XZZSO-72014/3104-S-JB-C274 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 26 | [12 empty] | Запись в БД произведена
1517 | 2202 | 3104 | 3104-MXI-77202A | SDO0001-01 | 3104-MXI-77202A |  | 3104-Z-7290 | 3104-MXI-77202A | SIS стоп мешалки второго преполим. 3104-AG-7202 | Second Pre-Polymerizer Agitator 3104-AG-7202 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7205 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 21 | [12 empty] | Запись в БД произведена
1519 | 2202 | Сombined Title | 3104-MXI-07203A | SDO0001-01 | 3104-MXI-07203A |  | 3104-Z-7210, 3104-Z-7290 | 3104-MXI-07203A | SIS стоп расплавного насоса второго преполим. 3104-P-7203A | Second Pre-Polymerizer Melt Pump 3104-P-7203A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7205 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 8 | [12 empty] | Запись в БД произведена
1520 | 2202 | 3104 | 3104-MII-07203 | SAI1000-01R | 3104-MII-07203 |  | 3104-Z-7210 | 3104-MII-07203 | Ток расплавного насоса второго преполим. 3104-P-7203A | Second Pre-Polymerizer Melt Pump 3104-P-7203A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7205 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 0 | [12 empty] | Запись в БД произведена
1522 | 2202 | Сombined Title | 3104-MXI-17203A | SDO0001-01 | 3104-MXI-17203A |  | 3104-Z-7211, 3104-Z-7290 | 3104-MXI-17203A | SIS стоп расплавного насоса второго преполим. 3104-P-7203B | Second Pre-Polymerizer Melt Pump 3104-P-7203B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7205 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 15 | [12 empty] | Запись в БД произведена
1523 | 2202 | 3104 | 3104-MII-17203 | SAI1000-01R | 3104-MII-17203 |  | 3104-Z-7211 | 3104-MII-17203 | Ток расплавного насоса второго преполим. 3104-P-7203B | Second Pre-Polymerizer Melt Pump 3104-P-7203B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7205 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 1 | [12 empty] | Запись в БД произведена
1525 | 3104 | Сombined Title | 3104-PZIA-72012A | SAI1000-01R | 3104-PZIA-72012A |  | 3104-Z-7210, 3104-Z-7211 | 3104-PZT-72012A | Р на входе 3104-R-7203 | 3104-R-7203 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,3 | 1,45 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C296/3000-S-MC-B02 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C296 |  |  | 3104-PZT-72012A/3104-S-JB-C296 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A11 | A12 | 03 | - | A11-03 | - | A12-03 | - | 7 | [12 empty] | Запись в БД произведена
1526 | 3104 | Сombined Title | 3104-PZIA-72012B | SAI1000-01R | 3104-PZIA-72012B |  | 3104-Z-7210, 3104-Z-7211 | 3104-PZT-72012B | Р на входе 3104-R-7203 | 3104-R-7203 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,3 | 1,45 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C309/3000-S-MC-B02 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C309 |  |  | 3104-PZT-72012B/3104-S-JB-C309 | 3000-S-SC-B01 | 3000-S-MC-B02 |  | A11 | A12 | 02 | - | A11-02 | - | A12-02 | - | 10 | [12 empty] | Запись в БД произведена
1527 | 3104 | Сombined Title | 3104-PZIA-72012C | SAI1000-01R | 3104-PZIA-72012C |  | 3104-Z-7210, 3104-Z-7211 | 3104-PZT-72012C | Р на входе 3104-R-7203 | 3104-R-7203 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7205 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 2 | MPaG | 0 | 2 | MPaG |  |  | 1,3 | 1,45 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C312/3000-S-MC-B03 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C312 |  |  | 3104-PZT-72012C/3104-S-JB-C312 | 3000-S-SC-B01 | 3000-S-MC-B03 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 3 | [12 empty] | Запись в БД произведена
1529 | 3104 | 3104 | 3104-PZIA-72015A | SAI1000-01R | 3104-PZIA-72015A |  | 3104-Z-7212, 3104-Z-7213 | 3104-PZT-72015A | Р нагнетания 3104-P-7205A/B | 3104-P-7205A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7206 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-PZT-72015A/3104-S-JB-C249 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 4 | [12 empty] | Запись в БД произведена
1530 | 3104 | 3104 | 3104-PZIA-72015B | SAI1000-01R | 3104-PZIA-72015B |  | 3104-Z-7212, 3104-Z-7213 | 3104-PZT-72015B | Р нагнетания 3104-P-7205A/B | 3104-P-7205A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7206 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-PZT-72015B/3104-S-JB-C261 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 8 | [12 empty] | Запись в БД произведена
1531 | 3104 | 3104 | 3104-PZIA-72015C | SAI1000-01R | 3104-PZIA-72015C |  | 3104-Z-7212, 3104-Z-7213 | 3104-PZT-72015C | Р нагнетания 3104-P-7205A/B | 3104-P-7205A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7206 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C262/3000-S-MC-B03 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C262 |  |  | 3104-PZT-72015C/3104-S-JB-C262 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 4 | [12 empty] | Запись в БД произведена
1533 | 3104 | Сombined Title | 3104-XZV-72061 | SKLPD0021-00 | 3104-XZV-72061 |  |  | 3104-XZV-72061 | PS к R-7202, отсечка подачи | PS to 3104-R-7202 cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7206 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1534 | 3104 | Сombined Title | 3104-XZV-72061 | SKLPD0021-00 | 3104-XZV-72061 |  | 3104-Z-7291 | 3104-XZY-72061 | PS к R-7202, отсечка подачи | PS to 3104-R-7202 cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7206 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR10 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3104-XZY-72061/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 19 | [12 empty] | Запись в БД произведена
1535 | 3104 | Сombined Title | 3104-XZV-72061 | SKLPD0021-00 | 3104-XZV-72061 |  |  | 3104-XZZSC-72061 | PS к R-7202, отсечка подачи (закрыт) | PS to 3104-R-7202 cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7206 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C301/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C301 |  |  | 3104-XZZSC-72061/3104-S-JB-C301 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 3 | [12 empty] | Запись в БД произведена
1536 | 3104 | Сombined Title | 3104-XZV-72061 | SKLPD0021-00 | 3104-XZV-72061 |  |  | 3104-XZZSO-72061 | PS к R-7202, отсечка подачи (открыт) | PS to 3104-R-7202 cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7206 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C301/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C301 |  |  | 3104-XZZSO-72061/3104-S-JB-C301 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 10 | - | A11-10 | - | A12-10 | - | 5 | [12 empty] | Запись в БД произведена
1538 | 2202 | 3104 | 3104-MXI-77203A | SDO0001-01 | 3104-MXI-77203A |  | 3104-Z-7290 | 3104-MXI-77203A | SIS стоп мешалки первого полимеризатора 3104-AG-7203 | First Polymerizer Agitator 3104-AG-7203 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7206 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 22 | [12 empty] | Запись в БД произведена
1540 | 2202 | 3104 | 3104-MXI-07205A | SDO0001-01 | 3104-MXI-07205A |  | 3104-Z-7212, 3104-Z-7290 | 3104-MXI-07205A | SIS стоп расплавного насоса первого полимеризатора 3104-P-7205A | First Polymerizer Melt Pump 3104-P-7205A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7206 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 10 | [12 empty] | Запись в БД произведена
1541 | 2202 | 3104 | 3104-MII-07205 | SAI1000-01R | 3104-MII-07205 |  | 3104-Z-7212 | 3104-MII-07205 | Ток расплавного насоса первого полимеризатора 3104-P-7205A | First Polymerizer Melt Pump 3104-P-7205A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7206 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 2 | [12 empty] | Запись в БД произведена
1543 | 2202 | 3104 | 3104-MXI-17205A | SDO0001-01 | 3104-MXI-17205A |  | 3104-Z-7213, 3104-Z-7290 | 3104-MXI-17205A | SIS стоп расплавного насоса первого полимеризатора 3104-P-7205B | First Polymerizer Melt Pump 3104-P-7205B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7206 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 17 | [12 empty] | Запись в БД произведена
1544 | 2202 | 3104 | 3104-MII-17205 | SAI1000-01R | 3104-MII-17205 |  | 3104-Z-7213 | 3104-MII-17205 | Ток расплавного насоса первого полимеризатора 3104-P-7205B | First Polymerizer Melt Pump 3104-P-7205B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7206 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 3 | [12 empty] | Запись в БД произведена
1546 | 3104 | 3104 | 3104-PZIA-72016A | SAI1000-01R | 3104-PZIA-72016A |  | 3104-Z-7212, 3104-Z-7213 | 3104-PZT-72016A | Р на входе 3104-R-7204 | 3104-R-7204 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C296/3000-S-MC-B02 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C296 |  |  | 3104-PZT-72016A/3104-S-JB-C296 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 2 | [12 empty] | Запись в БД произведена
1547 | 3104 | 3104 | 3104-PZIA-72016B | SAI1000-01R | 3104-PZIA-72016B |  | 3104-Z-7212, 3104-Z-7213 | 3104-PZT-72016B | Р на входе 3104-R-7204 | 3104-R-7204 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C309/3000-S-MC-B02 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C309 |  |  | 3104-PZT-72016B/3104-S-JB-C309 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 8 | [12 empty] | Запись в БД произведена
1548 | 3104 | 3104 | 3104-PZIA-72016C | SAI1000-01R | 3104-PZIA-72016C |  | 3104-Z-7212, 3104-Z-7213 | 3104-PZT-72016C | Р на входе 3104-R-7204 | 3104-R-7204 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C312/3000-S-MC-B03 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C312 |  |  | 3104-PZT-72016C/3104-S-JB-C312 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 03 | - | A21-03 | - | A22-03 | - | 1 | [12 empty] | Запись в БД произведена
1550 | 3104 | 3104 | 3104-PZIA-72019A | SAI1000-01R | 3104-PZIA-72019A |  | 3104-Z-7214, 3104-Z-7215 | 3104-PZT-72019A | Р нагнетания 3104-P-7206A/B | 3104-P-7206A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-PZT-72019A/3104-S-JB-C249 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 5 | [12 empty] | Запись в БД произведена
1551 | 3104 | 3104 | 3104-PZIA-72019B | SAI1000-01R | 3104-PZIA-72019B |  | 3104-Z-7214, 3104-Z-7215 | 3104-PZT-72019B | Р нагнетания 3104-P-7206A/B | 3104-P-7206A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-PZT-72019B/3104-S-JB-C261 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 9 | [12 empty] | Запись в БД произведена
1552 | 3104 | 3104 | 3104-PZIA-72019C | SAI1000-01R | 3104-PZIA-72019C |  | 3104-Z-7214, 3104-Z-7215 | 3104-PZT-72019C | Р нагнетания 3104-P-7206A/B | 3104-P-7206A/B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7207 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,45 | 1,5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C262/3000-S-MC-B03 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C262 |  |  | 3104-PZT-72019C/3104-S-JB-C262 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 5 | [12 empty] | Запись в БД произведена
1554 | 2202 | 3104 | 3104-MXI-77204A | SDO0001-01 | 3104-MXI-77204A |  | 3104-Z-7290 | 3104-MXI-77204A | SIS стоп мешалки второго полимеризатора 3104-AG-7204 | Second Polymerizer Agitator 3104-AG-7204 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7207 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 23 | [12 empty] | Запись в БД произведена
1556 | 2202 | 3104 | 3104-MXI-07206A | SDO0001-01 | 3104-MXI-07206A |  | 3104-Z-7214, 3104-Z-7290 | 3104-MXI-07206A | SIS стоп расплавного насоса второго полимеризатора 3104-P-7206A | Second Polymerizer Melt Pump 3104-P-7206A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7207 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 11 | [12 empty] | Запись в БД произведена
1557 | 2202 | 3104 | 3104-MII-07206 | SAI1000-01R | 3104-MII-07206 |  | 3104-Z-7214 | 3104-MII-07206 | Ток расплавного насоса второго полимеризатора 3104-P-7206A | Second Polymerizer Melt Pump 3104-P-7206A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7207 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 4 | [12 empty] | Запись в БД произведена
1559 | 2202 | 3104 | 3104-MXI-17206A | SDO0001-01 | 3104-MXI-17206A |  | 3104-Z-7215, 3104-Z-7290 | 3104-MXI-17206A | SIS стоп расплавного насоса второго полимеризатора 3104-P-7206B | Second Polymerizer Melt Pump 3104-P-7206B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7207 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 18 | [12 empty] | Запись в БД произведена
1560 | 2202 | 3104 | 3104-MII-17206 | SAI1000-01R | 3104-MII-17206 |  | 3104-Z-7215 | 3104-MII-17206 | Ток расплавного насоса второго полимеризатора 3104-P-7206B | Second Polymerizer Melt Pump 3104-P-7206B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7207 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 120 | A | 0 | 120 | A |  |  | 88 | 96 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 5 | [12 empty] | Запись в БД произведена
1562 | 3104 | 3104 | 3104-PZIA-72020A | SAI1000-01R | 3104-PZIA-72020A |  | 3104-Z-7214, 3104-Z-7215 | 3104-PZT-72020A | Р на входе 3104-R-7205 | 3104-R-7205 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C296/3000-S-MC-B02 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C296 |  |  | 3104-PZT-72020A/3104-S-JB-C296 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 02 | - | A21-02 | - | A22-02 | - | 3 | [12 empty] | Запись в БД произведена
1563 | 3104 | 3104 | 3104-PZIA-72020B | SAI1000-01R | 3104-PZIA-72020B |  | 3104-Z-7214, 3104-Z-7215 | 3104-PZT-72020B | Р на входе 3104-R-7205 | 3104-R-7205 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C309/3000-S-MC-B02 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C309 |  |  | 3104-PZT-72020B/3104-S-JB-C309 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 9 | [12 empty] | Запись в БД произведена
1564 | 3104 | 3104 | 3104-PZIA-72020C | SAI1000-01R | 3104-PZIA-72020C |  | 3104-Z-7214, 3104-Z-7215 | 3104-PZT-72020C | Р на входе 3104-R-7205 | 3104-R-7205 Inlet Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 1,7 | MPaG | 0 | 1,7 | MPaG |  |  | 1,2 | 1,35 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C312/3000-S-MC-B03 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 410 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C312 |  |  | 3104-PZT-72020C/3104-S-JB-C312 | 3000-S-SC-B02 | 3000-S-MC-B03 |  | A21 | A22 | 03 | - | A21-03 | - | A22-03 | - | 2 | [12 empty] | Запись в БД произведена
1566 | 3104 | 3104 | 3104-PZIA-72023A | SAI1000-01R | 3104-PZIA-72023A |  | 3104-Z-7216 | 3104-PZT-72023A | Р нагнетания 3104-P-7207A | 3104-P-7207A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-PZT-72023A/3104-S-JB-C249 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 6 | [12 empty] | Запись в БД произведена
1567 | 3104 | 3104 | 3104-PZIA-72023B | SAI1000-01R | 3104-PZIA-72023B |  | 3104-Z-7216 | 3104-PZT-72023B | Р нагнетания 3104-P-7207A | 3104-P-7207A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-PZT-72023B/3104-S-JB-C261 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 10 | [12 empty] | Запись в БД произведена
1568 | 3104 | 3104 | 3104-PZIA-72023C | SAI1000-01R | 3104-PZIA-72023C |  | 3104-Z-7216 | 3104-PZT-72023C | Р нагнетания 3104-P-7207A | 3104-P-7207A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C262/3000-S-MC-B03 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C262 |  |  | 3104-PZT-72023C/3104-S-JB-C262 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 6 | [12 empty] | Запись в БД произведена
1570 | 3104 | 3104 | 3104-PZIA-72024A | SAI1000-01R | 3104-PZIA-72024A |  | 3104-Z-7217 | 3104-PZT-72024A | Р нагнетания 3104-P-7207B | 3104-P-7207B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C249/3000-S-MC-B02 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 378 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C249 |  |  | 3104-PZT-72024A/3104-S-JB-C249 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 7 | [12 empty] | Запись в БД произведена
1571 | 3104 | 3104 | 3104-PZIA-72024B | SAI1000-01R | 3104-PZIA-72024B |  | 3104-Z-7217 | 3104-PZT-72024B | Р нагнетания 3104-P-7207B | 3104-P-7207B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C261/3000-S-MC-B02 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 431 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C261 |  |  | 3104-PZT-72024B/3104-S-JB-C261 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 00 | - | A21-00 | - | A22-00 | - | 11 | [12 empty] | Запись в БД произведена
1572 | 3104 | 3104 | 3104-PZIA-72024C | SAI1000-01R | 3104-PZIA-72024C |  | 3104-Z-7217 | 3104-PZT-72024C | Р нагнетания 3104-P-7207B | 3104-P-7207B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7208 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,9 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C262/3000-S-MC-B03 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C262 |  |  | 3104-PZT-72024C/3104-S-JB-C262 | 3000-S-SC-B02 | 3000-S-MC-B02 |  | A21 | A22 | 01 | - | A21-01 | - | A22-01 | - | 7 | [12 empty] | Запись в БД произведена
1574 | 3105 | Сombined Title | 3104-XZV-72081 | SKLPD0021-00 | 3104-XZV-72081 |  |  | 3104-XZV-72081 | PS к 3105-MX-7204, отсечка подачи | PS to 3105-MX-7204 cut off the feed | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7208 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1575 | 3105 | Сombined Title | 3104-XZV-72081 | SKLPD0021-00 | 3104-XZV-72081 |  | 3105-Z-7293 | 3104-XZY-72081 | PS к 3105-MX-7204, отсечка подачи | PS to 3105-MX-7204 cut off the feed | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7208 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR01 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3104-XZY-72081/3105-S-JB-D339 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 10 | [12 empty] | Запись в БД произведена
1576 | 3105 | Сombined Title | 3104-XZV-72081 | SKLPD0021-00 | 3104-XZV-72081 |  |  | 3104-XZZSC-72081 | PS к 3105-MX-7204, отсечка подачи (закрыт) | PS to 3105-MX-7204 cut off the feed | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7208 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C337/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 492 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C337 |  |  | 3104-XZZSC-72081/3105-S-JB-C337 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 2 | [12 empty] | Запись в БД произведена
1577 | 3105 | Сombined Title | 3104-XZV-72081 | SKLPD0021-00 | 3104-XZV-72081 |  |  | 3104-XZZSO-72081 | PS к 3105-MX-7204, отсечка подачи (открыт) | PS to 3105-MX-7204 cut off the feed | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7208 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C337/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 492 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C337 |  |  | 3104-XZZSO-72081/3105-S-JB-C337 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 3 | [12 empty] | Запись в БД произведена
1579 | 2202 | 3104 | 3104-MXI-77205A | SDO0001-01 | 3104-MXI-77205A |  | 3104-Z-7290 | 3104-MXI-77205A | SIS стоп мешалки третьего полимеризатора 3104-AG-7205 | Third Polymerizer Agitator 3104-AG-7205 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7208 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 24 | [12 empty] | Запись в БД произведена
1581 | 2202 | 3104 | 3104-MXI-07207A | SDO0001-01 | 3104-MXI-07207A |  | 3104-Z-7216, 3104-Z-7290 | 3104-MXI-07207A | SIS стоп расплавного насоса третьего полимеризатора 3104-P-7207A | Third Polymerizer Melt Pump 3104-P-7207A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7208 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 12 | [12 empty] | Запись в БД произведена
1582 | 2202 | 3104 | 3104-MII-07207 | SAI1000-01R | 3104-MII-07207 |  | 3104-Z-7216 | 3104-MII-07207 | Ток расплавного насоса третьего полимеризатора 3104-P-7207A | Third Polymerizer Melt Pump 3104-P-7207A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7208 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 230 | A | 0 | 230 | A |  |  | 170 | 186 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 6 | [12 empty] | Запись в БД произведена
1584 | 2202 | 3104 | 3104-MXI-17207A | SDO0001-01 | 3104-MXI-17207A |  | 3104-Z-7217, 3104-Z-7290 | 3104-MXI-17207A | SIS стоп расплавного насоса третьего полимеризатора 3104-P-7207B | Third Polymerizer Melt Pump 3104-P-7207B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7208 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 19 | [12 empty] | Запись в БД произведена
1585 | 2202 | 3104 | 3104-MII-17207 | SAI1000-01R | 3104-MII-17207 |  | 3104-Z-7217 | 3104-MII-17207 | Ток расплавного насоса третьего полимеризатора 3104-P-7207B | Third Polymerizer Melt Pump 3104-P-7207B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7208 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 230 | A | 0 | 230 | A |  |  | 170 | 186 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 7 | [12 empty] | Запись в БД произведена
1587 | 3105 | 3105 | 3105-PZIA-72026A | SAI1000-01R | 3105-PZIA-72026A |  | 3105-Z-7218 | 3105-PZT-72026A | Р нагнетания 3105-P-7208A | 3103-P-7208A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C327/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 497 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C327 |  |  | 3105-PZT-72026A/3105-S-JB-C327 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 9 | [12 empty] | Запись в БД произведена
1588 | 3105 | 3105 | 3105-PZIA-72026B | SAI1000-01R | 3105-PZIA-72026B |  | 3105-Z-7218 | 3105-PZT-72026B | Р нагнетания 3105-P-7208A | 3103-P-7208A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-PZT-72026B/3105-S-JB-C328 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 2 | [12 empty] | Запись в БД произведена
1589 | 3105 | 3105 | 3105-PZIA-72026C | SAI1000-01R | 3105-PZIA-72026C |  | 3105-Z-7218 | 3105-PZT-72026C | Р нагнетания 3105-P-7208A | 3103-P-7208A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C345/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 497 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C345 |  |  | 3105-PZT-72026C/3105-S-JB-C345 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 7 | [12 empty] | Запись в БД произведена
1591 | 3105 | 3105 | 3105-PZIA-72027A | SAI1000-01R | 3105-PZIA-72027A |  | 3105-Z-7219 | 3105-PZT-72027A | Р нагнетания 3105-P-7208B | 3103-P-7208B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C327/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 497 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C327 |  |  | 3105-PZT-72027A/3105-S-JB-C327 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 10 | [12 empty] | Запись в БД произведена
1592 | 3105 | 3105 | 3105-PZIA-72027B | SAI1000-01R | 3105-PZIA-72027B |  | 3105-Z-7219 | 3105-PZT-72027B | Р нагнетания 3105-P-7208B | 3103-P-7208B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-PZT-72027B/3105-S-JB-C328 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 3 | [12 empty] | Запись в БД произведена
1593 | 3105 | 3105 | 3105-PZIA-72027C | SAI1000-01R | 3105-PZIA-72027C |  | 3105-Z-7219 | 3105-PZT-72027C | Р нагнетания 3105-P-7208B | 3103-P-7208B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7209 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | MPaG | 0 | 6 | MPaG |  |  | 4,95 | 5 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C345/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 497 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C345 |  |  | 3105-PZT-72027C/3105-S-JB-C345 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 8 | [12 empty] | Запись в БД произведена
1595 | 2202 | 3105 | 3105-MXI-07208A | SDO0001-01 | 3105-MXI-07208A |  | 3105-Z-7218, 3105-Z-7292 | 3105-MXI-07208A | SIS стоп расплавного насоса основного дегазатора 3105-P-7208A | Main Devolatilizer Melt Pump 3105-P-7208A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7209 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 25 | [12 empty] | Запись в БД произведена
1596 | 2202 | 3105 | 3105-MII-07208 | SAI1000-01R | 3105-MII-07208 |  | 3105-Z-7218 | 3105-MII-07208 | Ток расплавного насоса основного дегазатора 3105-P-7208A | Main Devolatilizer Melt Pump 3105-P-7208A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7209 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 400 | A | 0 | 400 | A |  |  | 297 | 325 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 8 | [12 empty] | Запись в БД произведена
1598 | 2202 | 3105 | 3105-MXI-17208A | SDO0001-01 | 3105-MXI-17208A |  | 3105-Z-7219, 3105-Z-7292 | 3105-MXI-17208A | SIS стоп расплавного насоса основного дегазатора 3105-P-7208B | Main Devolatilizer Melt Pump 3105-P-7208B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7209 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 2 | [12 empty] | Запись в БД произведена
1599 | 2202 | 3105 | 3105-MII-17208 | SAI1000-01R | 3105-MII-17208 |  | 3105-Z-7219 | 3105-MII-17208 | Ток расплавного насоса основного дегазатора 3105-P-7208B | Main Devolatilizer Melt Pump 3105-P-7208B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7209 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 400 | A | 0 | 400 | A |  |  | 297 | 325 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 9 | [12 empty] | Запись в БД произведена
1601 | 3105 | 3105 | 3105-PZIA-72030A | SAI1000-01R | 3105-PZIA-72030A |  | 3105-Z-7220 | 3105-PZT-72030A | Р нагнетания 3105-P-7209A | 3103-P-7209A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C327/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 497 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C327 |  |  | 3105-PZT-72030A/3105-S-JB-C327 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 11 | [12 empty] | Запись в БД произведена
1602 | 3105 | 3105 | 3105-PZIA-72030B | SAI1000-01R | 3105-PZIA-72030B |  | 3105-Z-7220 | 3105-PZT-72030B | Р нагнетания 3105-P-7209A | 3103-P-7209A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-PZT-72030B/3105-S-JB-C328 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 4 | [12 empty] | Запись в БД произведена
1603 | 3105 | 3105 | 3105-PZIA-72030C | SAI1000-01R | 3105-PZIA-72030C |  | 3105-Z-7220 | 3105-PZT-72030C | Р нагнетания 3105-P-7209A | 3103-P-7209A Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C345/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 497 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C345 |  |  | 3105-PZT-72030C/3105-S-JB-C345 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 9 | [12 empty] | Запись в БД произведена
1605 | 3105 | 3105 | 3105-PZIA-72031A | SAI1000-01R | 3105-PZIA-72031A |  | 3105-Z-7221 | 3105-PZT-72031A | Р нагнетания 3105-P-7209B | 3103-P-7209B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C327/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 497 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C327 |  |  | 3105-PZT-72031A/3105-S-JB-C327 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 13 | [12 empty] | Запись в БД произведена
1606 | 3105 | 3105 | 3105-PZIA-72031B | SAI1000-01R | 3105-PZIA-72031B |  | 3105-Z-7221 | 3105-PZT-72031B | Р нагнетания 3105-P-7209B | 3103-P-7209B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-PZT-72031B/3105-S-JB-C328 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 6 | [12 empty] | Запись в БД произведена
1607 | 3105 | 3105 | 3105-PZIA-72031C | SAI1000-01R | 3105-PZIA-72031C |  | 3105-Z-7221 | 3105-PZT-72031C | Р нагнетания 3105-P-7209B | 3103-P-7209B Discharge Pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 20 | MPaG | 0 | 20 | MPaG |  |  | 18,4 | 19 |  | MPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C345/3000-S-MC-B01 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 497 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C345 |  |  | 3105-PZT-72031C/3105-S-JB-C345 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 11 | [12 empty] | Запись в БД произведена
1609 | 3105 | 3105 | 3105-TZIA-72045A | SAI1000-01R | 3105-TZIA-72045A |  | 3105-Z-7220 | 3105-TZT-72045A | Т на выходе 3105-P-7209A | 3105-P-7209A outlet temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C327/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 497 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C327 |  |  | 3105-TZT-72045A/3105-S-JB-C327 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 12 | [12 empty] | Запись в БД произведена
1610 | 3105 | 3105 | 3105-TZIA-72045B | SAI1000-01R | 3105-TZIA-72045B |  | 3105-Z-7220 | 3105-TZT-72045B | Т на выходе 3105-P-7209A | 3105-P-7209A outlet temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-TZT-72045B/3105-S-JB-C328 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 5 | [12 empty] | Запись в БД произведена
1611 | 3105 | 3105 | 3105-TZIA-72045C | SAI1000-01R | 3105-TZIA-72045C |  | 3105-Z-7220 | 3105-TZT-72045C | Т на выходе 3105-P-7209A | 3105-P-7209A outlet temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C345/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 497 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C345 |  |  | 3105-TZT-72045C/3105-S-JB-C345 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 10 | [12 empty] | Запись в БД произведена
1613 | 3105 | 3105 | 3105-TZIA-72047A | SAI1000-01R | 3105-TZIA-72047A |  | 3105-Z-7221 | 3105-TZT-72047A | Т на выходе 3105-P-7209B | 3105-P-7209B outlet temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C327/3000-S-MC-B01 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 497 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C327 |  |  | 3105-TZT-72047A/3105-S-JB-C327 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 14 | [12 empty] | Запись в БД произведена
1614 | 3105 | 3105 | 3105-TZIA-72047B | SAI1000-01R | 3105-TZIA-72047B |  | 3105-Z-7221 | 3105-TZT-72047B | Т на выходе 3105-P-7209B | 3105-P-7209B outlet temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-TZT-72047B/3105-S-JB-C328 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 7 | [12 empty] | Запись в БД произведена
1615 | 3105 | 3105 | 3105-TZIA-72047C | SAI1000-01R | 3105-TZIA-72047C |  | 3105-Z-7221 | 3105-TZT-72047C | Т на выходе 3105-P-7209B | 3105-P-7209B outlet temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7210 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,5 | -50 | 350 | ℃ | -50 | 350 | ℃ | 150 | 190 |  |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C345/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 497 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C345 |  |  | 3105-TZT-72047C/3105-S-JB-C345 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 12 | [12 empty] | Запись в БД произведена
1617 | 2202 | 3105 | 3105-MXI-07209A | SDO0001-01 | 3105-MXI-07209A |  | 3105-Z-7220, 3105-Z-7292 | 3105-MXI-07209A | SIS стоп расплавного насоса финального дегазатора 3105-P-7209A | Final Devolatilizer Melt Pump 3105-P-7209A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7210 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 26 | [12 empty] | Запись в БД произведена
1618 | 2202 | 3105 | 3105-MII-07209 | SAI1000-01R | 3105-MII-07209 |  | 3105-Z-7220 | 3105-MII-07209 | Ток расплавного насоса финального дегазатора 3105-P-7209A | Final Devolatilizer Melt Pump 3105-P-7209A Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7210 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 450 | A | 0 | 450 | A |  |  | 344 | 375 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 10 | [12 empty] | Запись в БД произведена
1620 | 2202 | 3105 | 3105-MXI-17209A | SDO0001-01 | 3105-MXI-17209A |  | 3105-Z-7221, 3105-Z-7292 | 3105-MXI-17209A | SIS стоп расплавного насоса финального дегазатора 3105-P-7209B | Final Devolatilizer Melt Pump 3105-P-7209B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7210 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 3 | [12 empty] | Запись в БД произведена
1621 | 2202 | 3105 | 3105-MII-17209 | SAI1000-01R | 3105-MII-17209 |  | 3105-Z-7221 | 3105-MII-17209 | Ток расплавного насоса финального дегазатора 3105-P-7209B | Final Devolatilizer Melt Pump 3105-P-7209B Current | Current | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7210 | MCC | AIR-EP | Non-Ex | SIS | I | 24V DC 2-wire | ≤1 | 0 | 450 | A | 0 | 450 | A |  |  | 344 | 375 |  | A | REV 2/REV 5 | Update Ex.type to Non-Ex, I/O Type to AIR-LP/Update Instument type/I/O Type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A72 | A73 | 05 | - | A72-05 | - | A73-05 | - | 11 | [12 empty] | Запись в БД произведена
1623 | 3105 | 3105 | 3105-LZSA-72010 | SDI0010-01R | 3105-LZSA-72010 |  | 3105-Z-7224 | 3105-LZS-72010 | Ур. на входе 3105-P-7210A | 3105-P-7210A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C330/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 453 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C330 |  |  | 3105-LZS-72010/3105-S-JB-C330 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 8 | [12 empty] | Запись в БД произведена
1625 | 3105 | 3105 | 3105-LZSA-72011 | SDI0010-01R | 3105-LZSA-72011 |  | 3105-Z-7224 | 3105-LZS-72011 | Ур. на входе 3105-P-7210B | 3105-P-7210B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C330/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 453 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C330 |  |  | 3105-LZS-72011/3105-S-JB-C330 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 9 | [12 empty] | Запись в БД произведена
1627 | 3105 | 3105 | 3105-XZV-72117 | SKLPD0021-00 | 3105-XZV-72117 |  |  | 3105-XZV-72117 | Вход 3105-P-7210 | 3105-P-7210 Inlet | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1628 | 3105 | 3105 | 3105-XZV-72117 | SKLPD0021-00 | 3105-XZV-72117 |  | 3105-Z-7240 | 3105-XZY-72117 | Вход 3105-P-7210 | 3105-P-7210 Inlet | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR11 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72117/3105-S-JB-D339 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 9 | [12 empty] | Запись в БД произведена
1629 | 3105 | 3105 | 3105-XZV-72117 | SKLPD0021-00 | 3105-XZV-72117 |  |  | 3105-XZZSC-72117 | Вход 3105-P-7210 (закрыт) | 3105-P-7210 Inlet | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR13 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSC-72117/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 30 | [12 empty] | Запись в БД произведена
1630 | 3105 | 3105 | 3105-XZV-72117 | SKLPD0021-00 | 3105-XZV-72117 |  |  | 3105-XZZSO-72117 | Вход 3105-P-7210 (открыт) | 3105-P-7210 Inlet | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR14 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSO-72117/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 3 | [12 empty] | Запись в БД произведена
1632 | 3105 | 3105 | 3105-XZV-72118 | SKLPD0021-00 | 3105-XZV-72118 |  |  | 3105-XZV-72118 | Выход 3105-P-7210 | 3105-P-7210 Outlet | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1633 | 3105 | 3105 | 3105-XZV-72118 | SKLPD0021-00 | 3105-XZV-72118 |  | 3105-Z-7240 | 3105-XZY-72118 | Выход 3105-P-7210 | 3105-P-7210 Outlet | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR10 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72118/3105-S-JB-D339 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 10 | [12 empty] | Запись в БД произведена
1634 | 3105 | 3105 | 3105-XZV-72118 | SKLPD0021-00 | 3105-XZV-72118 |  |  | 3105-XZZSC-72118 | Выход 3105-P-7210 (закрыт) | 3105-P-7210 Outlet | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSC-72118/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 31 | [12 empty] | Запись в БД произведена
1635 | 3105 | 3105 | 3105-XZV-72118 | SKLPD0021-00 | 3105-XZV-72118 |  |  | 3105-XZZSO-72118 | Выход 3105-P-7210 (открыт) | 3105-P-7210 Outlet | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSO-72118/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 4 | [12 empty] | Запись в БД произведена
1637 | 3105 | 3105 | 3105-PZIA-72045 | SAI1000-01R | 3105-PZIA-72045 |  | 3105-Z-7231 | 3105-PZT-72045 | Р на входе 3105-PK-7213A/B | 3105-PK-7213A/B inlet pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | kPaA | 0 | 6 | kPaA |  |  | 1 | 1,5 |  | kPaA | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3105-PZT-72045/3000-S-MC-B04 |  | NH-IA-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B04 | Одиночный |  | 3105-PZT-72045/3000-S-MC-B04 | 3000-S-SC-B03 | 3000-S-MC-B04 |  | A31 | A32 | 06 | - | A31-06 | - | A32-06 | - | 8 | [12 empty] | Запись в БД произведена
1639 | 3105 |  | 3105-XZV-72025 | SKLPD0021-00 | 3105-XZV-72025 |  |  | 3105-XZV-72025 | Поток N2 к 3105-PK-7213AB | N2 flow to 3105-PK-7213AB | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
1640 | 3105 | 3105 | 3105-XZV-72025 | SKLPD0021-00 | 3105-XZV-72025 |  | 3105-Z-7231 | 3105-XZY-72025 | Поток N2 к 3105-PK-7213AB | N2 flow to 3105-PK-7213AB | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3105-XZY-72025/3000-S-MC-B14 |  | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B14 | Одиночный |  | 3105-XZY-72025/3000-S-MC-B14 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 19 | [12 empty] | Запись в БД произведена
1641 | 3105 | 3105 | 3105-XZV-72025 | SKLPD0021-00 | 3105-XZV-72025 |  |  | 3105-XZZSC-72025 | Поток N2 к 3105-PK-7213AB (закрыт) | N2 flow to 3105-PK-7213AB | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3105-XZZSC-72025/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3105-XZZSC-72025/3000-S-MC-B08 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 23 | [12 empty] | Запись в БД произведена
1642 | 3105 | 3105 | 3105-XZV-72025 | SKLPD0021-00 | 3105-XZV-72025 |  |  | 3105-XZZSO-72025 | Поток N2 к 3105-PK-7213AB (открыт) | N2 flow to 3105-PK-7213AB | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7211 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3105-XZZSO-72025/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3105-XZZSO-72025/3000-S-MC-B08 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 26 | [12 empty] | Запись в БД произведена
1644 | 2202 | 3105 | 3105-MXI-07210A | SDO0001-01 | 3105-MXI-07210A |  | 3105-Z-7224, 3105-Z-7240, 3105-Z-7292 | 3105-MXI-07210A | SIS стоп насоса конденсата финального дегазатора 3105-P-7210A | Final Devolatilizer Condensate Pump 3105-P-7210A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7211 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 27 | [12 empty] | Запись в БД произведена
1646 | 2202 | 3105 | 3105-MXI-17210A | SDO0001-01 | 3105-MXI-17210A |  | 3105-Z-7224, 3105-Z-7240, 3105-Z-7292 | 3105-MXI-17210A | SIS стоп насоса конденсата финального дегазатора 3105-P-7210B | Final Devolatilizer Condensate Pump 3105-P-7210B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7211 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 4 | [12 empty] | Запись в БД произведена
1648 | 3105 | 3105 | 3105-LZSA-72033A | SDI0010-01R | 3105-LZSA-72033A |  | 3105-Z-7225 | 3105-LZS-72033A | Ур. на входе 3105-P-7211A | 3105-P-7211A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C324/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C324 |  |  | 3105-LZS-72033A/3105-S-JB-C324 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 26 | [12 empty] | Запись в БД произведена
1650 | 3105 | 3105 | 3105-LZSA-72033B | SDI0010-01R | 3105-LZSA-72033B |  | 3105-Z-7225 | 3105-LZS-72033B | Ур. на входе 3105-P-7211B | 3105-P-7211B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C323/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C323 |  |  | 3105-LZS-72033B/3105-S-JB-C323 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 20 | [12 empty] | Запись в БД произведена
1652 | 3105 | Сombined Title | 3105-XZV-72105 | SKLPD0021-00 | 3105-XZV-72105 |  |  | 3105-XZV-72105 | Вход 3105-P-7211AB | 3105-P-7211AB Inlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1653 | 3105 | Сombined Title | 3105-XZV-72105 | SKLPD0021-00 | 3105-XZV-72105 |  | 3105-Z-7241 | 3105-XZY-72105 | Вход 3105-P-7211AB | 3105-P-7211AB Inlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR01 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3105-XZY-72105/3105-S-JB-D332 | 3000-S-SC-B01 | 3000-S-MC-B13 |  | A13 | A14 | 04 | 05 | A13-04 | A13-05 | A14-04 | A14-05 | 14 | [12 empty] | Запись в БД произведена
1654 | 3105 | Сombined Title | 3105-XZV-72105 | SKLPD0021-00 | 3105-XZV-72105 |  |  | 3105-XZZSC-72105 | Вход 3105-P-7211AB (закрыт) | 3105-P-7211AB Inlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3105-XZZSC-72105/3105-S-JB-C329 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 0 | [12 empty] | Запись в БД произведена
1655 | 3105 | Сombined Title | 3105-XZV-72105 | SKLPD0021-00 | 3105-XZV-72105 |  |  | 3105-XZZSO-72105 | Вход 3105-P-7211AB (открыт) | 3105-P-7211AB Inlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3105-XZZSO-72105/3105-S-JB-C329 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 1 | [12 empty] | Запись в БД произведена
1657 | 3105 | Сombined Title | 3105-XZV-72106 | SKLPD0021-00 | 3105-XZV-72106 |  |  | 3105-XZV-72106 | Выход 3105-P-7211AB | 3105-P-7211AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1658 | 3105 | Сombined Title | 3105-XZV-72106 | SKLPD0021-00 | 3105-XZV-72106 |  | 3105-Z-7241, 3105-Z-7293 | 3105-XZY-72106 | Выход 3105-P-7211AB | 3105-P-7211AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR02 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72106/3105-S-JB-D339 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 11 | [12 empty] | Запись в БД произведена
1659 | 3105 | Сombined Title | 3105-XZV-72106 | SKLPD0021-00 | 3105-XZV-72106 |  |  | 3105-XZZSC-72106 | Выход 3105-P-7211AB (закрыт) | 3105-P-7211AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C337/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 492 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C337 |  |  | 3105-XZZSC-72106/3105-S-JB-C337 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 4 | [12 empty] | Запись в БД произведена
1660 | 3105 | Сombined Title | 3105-XZV-72106 | SKLPD0021-00 | 3105-XZV-72106 |  |  | 3105-XZZSO-72106 | Выход 3105-P-7211AB (открыт) | 3105-P-7211AB Outlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C337/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 492 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C337 |  |  | 3105-XZZSO-72106/3105-S-JB-C337 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 7 | [12 empty] | Запись в БД произведена
1662 | 3105 | Сombined Title | 3105-TZIA-66356A | SAI1000-01R | 3105-TZIA-66356A |  | 3105-Z-7241 | 3105-TZT-66356A | Т подшипника 3105-P-7211A | 3105-P-7211A Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C327/3000-S-MC-B01 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 497 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C327 |  |  | 3105-TZT-66356A/3105-S-JB-C327 | 3000-S-SC-B01 | 3000-S-MC-B01 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 12 | [12 empty] | Запись в БД произведена
1663 | 2202 | 3105 | 3105-MXI-07211A | SDO0001-01 | 3105-MXI-07211A |  | 3105-Z-7225, 3105-Z-7241, 3105-Z-7292 | 3105-MXI-07211A | SIS стоп кубового насоса колонны очистки 3105-P-7211A | Purification Column Kettle Pump 3105-P-7211A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7212 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 28 | [12 empty] | Запись в БД произведена
1665 | 3105 | Сombined Title | 3105-TZIA-66356B | SAI1000-01R | 3105-TZIA-66356B |  | 3105-Z-7241 | 3105-TZT-66356B | Т подшипника 3105-P-7211B | 3105-P-7211B Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7212 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-TZT-66356B/3105-S-JB-C328 | 3000-S-SC-B01 | 3000-S-MC-B01 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 14 | [12 empty] | Запись в БД произведена
1666 | 2202 | 3105 | 3105-MXI-17211A | SDO0001-01 | 3105-MXI-17211A |  | 3105-Z-7225, 3105-Z-7241, 3105-Z-7292 | 3105-MXI-17211A | SIS стоп кубового насоса колонны очистки 3105-P-7211B | Purification Column Kettle Pump 3105-P-7211B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7212 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 5 | [12 empty] | Запись в БД произведена
1668 | 3105 | 3105 | 3105-LZSA-72034A | SDI0010-01R | 3105-LZSA-72034A |  | 3105-Z-7226 | 3105-LZS-72034A | Ур. на входе 3105-P-7212A | 3105-P-7212A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C324/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C324 |  |  | 3105-LZS-72034A/3105-S-JB-C324 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 27 | [12 empty] | Запись в БД произведена
1670 | 3105 | 3105 | 3105-LZSA-72034B | SDI0010-01R | 3105-LZSA-72034B |  | 3105-Z-7226 | 3105-LZS-72034B | Ур. на входе 3105-P-7212B | 3105-P-7212B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C323/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C323 |  |  | 3105-LZS-72034B/3105-S-JB-C323 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 21 | [12 empty] | Запись в БД произведена
1672 | 3105 | 3105 | 3105-XZV-72107 | SKLPD0021-00 | 3105-XZV-72107 |  |  | 3105-XZV-72107 | Вход 3105-P-7212AB | 3105-P-7212AB Inlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7213 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1673 | 3105 | Сombined Title | 3105-XZV-72107 | SKLPD0021-00 | 3105-XZV-72107 |  | 3105-Z-7242 | 3105-XZY-72107 | Вход 3105-P-7212AB | 3105-P-7212AB Inlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7213 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR03 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72107/3105-S-JB-D339 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 12 | [12 empty] | Запись в БД произведена
1674 | 3105 | Сombined Title | 3105-XZV-72107 | SKLPD0021-00 | 3105-XZV-72107 |  |  | 3105-XZZSC-72107 | Вход 3105-P-7212AB (закрыт) | 3105-P-7212AB Inlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C337/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 492 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C337 |  |  | 3105-XZZSC-72107/3105-S-JB-C337 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 5 | [12 empty] | Запись в БД произведена
1675 | 3105 | Сombined Title | 3105-XZV-72107 | SKLPD0021-00 | 3105-XZV-72107 |  |  | 3105-XZZSO-72107 | Вход 3105-P-7212AB (открыт) | 3105-P-7212AB Inlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C337/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 492 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C337 |  |  | 3105-XZZSO-72107/3105-S-JB-C337 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 8 | [12 empty] | Запись в БД произведена
1677 | 3105 | Сombined Title | 3105-XZV-72108 | SKLPD0021-00 | 3105-XZV-72108 |  |  | 3105-XZV-72108 | Выход 3105-P-7212AB | 3105-P-7212AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7213 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1678 | 3105 | Сombined Title | 3105-XZV-72108 | SKLPD0021-00 | 3105-XZV-72108 |  | 3105-Z-7242, 3105-Z-7293 | 3105-XZY-72108 | Выход 3105-P-7212AB | 3105-P-7212AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7213 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR04 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72108/3105-S-JB-D339 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 13 | [12 empty] | Запись в БД произведена
1679 | 3105 | Сombined Title | 3105-XZV-72108 | SKLPD0021-00 | 3105-XZV-72108 |  |  | 3105-XZZSC-72108 | Выход 3105-P-7212AB (закрыт) | 3105-P-7212AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C337/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 492 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C337 |  |  | 3105-XZZSC-72108/3105-S-JB-C337 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 6 | [12 empty] | Запись в БД произведена
1680 | 3105 | Сombined Title | 3105-XZV-72108 | SKLPD0021-00 | 3105-XZV-72108 |  |  | 3105-XZZSO-72108 | Выход 3105-P-7212AB (открыт) | 3105-P-7212AB Outlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C337/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 492 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C337 |  |  | 3105-XZZSO-72108/3105-S-JB-C337 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 9 | [12 empty] | Запись в БД произведена
1682 | 3105 | 3105 | 3105-PZIA-72046 | SAI1000-01R | 3105-PZIA-72046 |  | 3105-Z-7232 | 3105-PZT-72046 | Р на выходе VG из 3105-E-7207 | 3105-E-7207 VG outlet pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7213 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 6 | kPaA | 0 | 6 | kPaA |  |  | 4 | 5 |  | kPaA | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3105-PZT-72046/3000-S-MC-B04 |  | NH-IA-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B04 | Одиночный |  | 3105-PZT-72046/3000-S-MC-B04 | 3000-S-SC-B03 | 3000-S-MC-B04 |  | A31 | A32 | 06 | - | A31-06 | - | A32-06 | - | 9 | [12 empty] | Запись в БД произведена
1684 | 3105 | 3105 | 3105-XZV-72026 | SKLPD0021-00 | 3105-XZV-72026 |  |  | 3105-XZV-72026 | Поток N2 к 3105-PK-7213AB | N2 flow to 3105-PK-7213AB | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7213 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
1685 | 3105 | 3105 | 3105-XZV-72026 | SKLPD0021-00 | 3105-XZV-72026 |  | 3105-Z-7232 | 3105-XZY-72026 | Поток N2 к 3105-PK-7213AB | N2 flow to 3105-PK-7213AB | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7213 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3105-XZY-72026/3000-S-MC-B14 |  | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B14 | Одиночный |  | 3105-XZY-72026/3000-S-MC-B14 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 20 | [12 empty] | Запись в БД произведена
1686 | 3105 | 3105 | 3105-XZV-72026 | SKLPD0021-00 | 3105-XZV-72026 |  |  | 3105-XZZSC-72026 | Поток N2 к 3105-PK-7213AB (закрыт) | N2 flow to 3105-PK-7213AB | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3105-XZZSC-72026/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3105-XZZSC-72026/3000-S-MC-B08 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 24 | [12 empty] | Запись в БД произведена
1687 | 3105 | 3105 | 3105-XZV-72026 | SKLPD0021-00 | 3105-XZV-72026 |  |  | 3105-XZZSO-72026 | Поток N2 к 3105-PK-7213AB (открыт) | N2 flow to 3105-PK-7213AB | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7213 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3105-XZZSO-72026/3000-S-MC-B08 |  | NH-IA-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B08 | Одиночный |  | 3105-XZZSO-72026/3000-S-MC-B08 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 27 | [12 empty] | Запись в БД произведена
1689 | 2202 | 3105 | 3105-MXI-07212A | SDO0001-01 | 3105-MXI-07212A |  | 3105-Z-7226, 3105-Z-7242, 3105-Z-7292 | 3105-MXI-07212A | SIS стоп насоса рецикла колонны очистки 3105-P-7212A | Purification Column Reflux Pump 3105-P-7212A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7213 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 29 | [12 empty] | Запись в БД произведена
1691 | 2202 | 3105 | 3105-MXI-17212A | SDO0001-01 | 3105-MXI-17212A |  | 3105-Z-7226, 3105-Z-7242, 3105-Z-7292 | 3105-MXI-17212A | SIS стоп насоса рецикла колонны очистки 3105-P-7212B | Purification Column Reflux Pump 3105-P-7212B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7213 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 6 | [12 empty] | Запись в БД произведена
1693 | 3104 | 3104 | 3104-PZIA-72047 | SAI1000-01R | 3104-PZIA-72047 |  | 3105-Z-7233 | 3104-PZT-72047 | Р на входе 3105-PK-6215 | 3105-PK-6215 inlet pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7214 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 150 | kPaA | 0 | 150 | kPaA |  |  | 60 | 80 |  | kPaA | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C296/3000-S-MC-B02 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 410 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C296 |  |  | 3104-PZT-72047/3104-S-JB-C296 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 2 | [12 empty] | Запись в БД произведена
1695 | 3104 | 3104 | 3105-XZV-72030 | SKLPD0021-00 | 3105-XZV-72030 |  |  | 3105-XZV-72030 | Поток N2 к 3105-PK-7215 | N2 flow to 3105-PK-7215 | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7214 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
1696 | 3104 | 3104 | 3105-XZV-72030 | SKLPD0021-00 | 3105-XZV-72030 |  | 3105-Z-7233 | 3105-XZY-72030 | Поток N2 к 3105-PK-7215 | N2 flow to 3105-PK-7215 | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7214 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-D320/3000-S-MC-B11 | PR05 | NH-KYJYP3 16x2.5 | 396 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D320 |  |  | 3105-XZY-72030/3104-S-JB-D320 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 15 | [12 empty] | Запись в БД произведена
1697 | 3104 | 3104 | 3105-XZV-72030 | SKLPD0021-00 | 3105-XZV-72030 |  |  | 3105-XZZSC-72030 | Поток N2 к 3105-PK-7215 (закрыт) | N2 flow to 3105-PK-7215 | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7214 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3105-XZZSC-72030/3104-S-JB-C306 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 30 | [12 empty] | Запись в БД произведена
1698 | 3104 | 3104 | 3105-XZV-72030 | SKLPD0021-00 | 3105-XZV-72030 |  |  | 3105-XZZSO-72030 | Поток N2 к 3105-PK-7215 (открыт) | N2 flow to 3105-PK-7215 | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7214 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C306/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 396 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C306 |  |  | 3105-XZZSO-72030/3104-S-JB-C306 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 31 | [12 empty] | Запись в БД произведена
1700 | 3105 | 3105 | 3105-LZSA-72037A | SDI0010-01R | 3105-LZSA-72037A |  | 3105-Z-7227 | 3105-LZS-72037A | Ур. на входе 3105-P-7218A | 3105-P-7218A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C330/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 453 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C330 |  |  | 3105-LZS-72037A/3105-S-JB-C330 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 11 | [12 empty] | Запись в БД произведена
1702 | 3105 | 3105 | 3105-LZSA-72037B | SDI0010-01R | 3105-LZSA-72037B |  | 3105-Z-7227 | 3105-LZS-72037B | Ур. на входе 3105-P-7218B | 3105-P-7218B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3105-LZS-72037B/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 18 | [12 empty] | Запись в БД произведена
1704 | 3104 | Сombined Title | 3105-LZSA-72038A | SDI0010-01R | 3105-LZSA-72038A |  | 3105-Z-7228 | 3105-LZS-72038A | Ур. на входе 3105-P-7219A | 3105-P-7219A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C272/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C272 |  |  | 3105-LZS-72038A/3104-S-JB-C272 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 15 | [12 empty] | Запись в БД произведена
1706 | 3104 | Сombined Title | 3105-LZSA-72038B | SDI0010-01R | 3105-LZSA-72038B |  | 3105-Z-7228 | 3105-LZS-72038B | Ур. на входе 3105-P-7219B | 3105-P-7219B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR13 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3105-LZS-72038B/3104-S-JB-C274 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 27 | [12 empty] | Запись в БД произведена
1708 | 3105 | Сombined Title | 3105-XZV-72113 | SKLPD0021-00 | 3105-XZV-72113 |  |  | 3105-XZV-72113 | Вход 3105-P-7218AB | 3105-P-7218AB Intlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1709 | 3105 | Сombined Title | 3105-XZV-72113 | SKLPD0021-00 | 3105-XZV-72113 |  | 3105-Z-7243 | 3105-XZY-72113 | Вход 3105-P-7218AB | 3105-P-7218AB Intlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR08 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72113/3105-S-JB-D339 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 14 | [12 empty] | Запись в БД произведена
1710 | 3105 | Сombined Title | 3105-XZV-72113 | SKLPD0021-00 | 3105-XZV-72113 |  |  | 3105-XZZSC-72113 | Вход 3105-P-7218AB (закрыт) | 3105-P-7218AB Intlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSC-72113/3105-S-JB-C338 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 10 | [12 empty] | Запись в БД произведена
1711 | 3105 | Сombined Title | 3105-XZV-72113 | SKLPD0021-00 | 3105-XZV-72113 |  |  | 3105-XZZSO-72113 | Вход 3105-P-7218AB (открыт) | 3105-P-7218AB Intlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSO-72113/3105-S-JB-C338 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 12 | [12 empty] | Запись в БД произведена
1713 | 3105 | Сombined Title | 3105-XZV-72114 | SKLPD0021-00 | 3105-XZV-72114 |  |  | 3105-XZV-72114 | Выход 3105-P-7218AB | 3105-P-7218AB Outlet | On-Off Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1714 | 3105 | Сombined Title | 3105-XZV-72114 | SKLPD0021-00 | 3105-XZV-72114 |  | 3105-Z-7243, 3105-Z-7293 | 3105-XZY-72114 | Выход 3105-P-7218AB | 3105-P-7218AB Outlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR09 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72114/3105-S-JB-D339 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A13 | A14 | 00 | 01 | A13-00 | A13-01 | A14-00 | A14-01 | 15 | [12 empty] | Запись в БД произведена
1715 | 3105 | Сombined Title | 3105-XZV-72114 | SKLPD0021-00 | 3105-XZV-72114 |  |  | 3105-XZZSC-72114 | Выход 3105-P-7218AB (закрыт) | 3105-P-7218AB Outlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSC-72114/3105-S-JB-C338 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 11 | [12 empty] | Запись в БД произведена
1716 | 3105 | Сombined Title | 3105-XZV-72114 | SKLPD0021-00 | 3105-XZV-72114 |  |  | 3105-XZZSO-72114 | Выход 3105-P-7218AB (открыт) | 3105-P-7218AB Outlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSO-72114/3105-S-JB-C338 | 3000-S-SC-B01 | 3000-S-MC-B05 |  | A11 | A12 | 05 | - | A11-05 | - | A12-05 | - | 13 | [12 empty] | Запись в БД произведена
1718 | 3104 | Сombined Title | 3105-XZV-72115 | SKLPD0021-00 | 3105-XZV-72115 |  |  | 3105-XZV-72115 | Вход 3105-P-7219AB | 3105-P-7219AB Intlet | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1719 | 3104 | Сombined Title | 3105-XZV-72115 | SKLPD0021-00 | 3105-XZV-72115 |  | 3105-Z-7244 | 3105-XZY-72115 | Вход 3105-P-7219AB | 3105-P-7219AB Intlet | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D286/3000-S-MC-B14 | PR09 | NH-KYJYP3 24x2.5 | 378 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D286 |  |  | 3105-XZY-72115/3104-S-JB-D286 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 24 | [12 empty] | Запись в БД произведена
1720 | 3104 | Сombined Title | 3105-XZV-72115 | SKLPD0021-00 | 3105-XZV-72115 |  |  | 3105-XZZSC-72115 | Вход 3105-P-7219AB (закрыт) | 3105-P-7219AB Intlet | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C282/3000-S-MC-B08 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 378 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C282 |  |  | 3105-XZZSC-72115/3104-S-JB-C282 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 3 | [12 empty] | Запись в БД произведена
1721 | 3104 | Сombined Title | 3105-XZV-72115 | SKLPD0021-00 | 3105-XZV-72115 |  |  | 3105-XZZSO-72115 | Вход 3105-P-7219AB (открыт) | 3105-P-7219AB Intlet | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C282/3000-S-MC-B08 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 378 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C282 |  |  | 3105-XZZSO-72115/3104-S-JB-C282 | 3000-S-SC-B01 | 3000-S-MC-B08 |  | A11 | A12 | 11 | - | A11-11 | - | A12-11 | - | 4 | [12 empty] | Запись в БД произведена
1723 | 3104 | Сombined Title | 3105-XZV-72029 | SKLPD0021-00 | 3105-XZV-72029 |  |  | 3105-XZV-72029 | Отс. клап. 3105-P-7219A/B к 3104-MX-7201 | 3105-P-7219A/B to 3104-MX-7201 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1724 | 3104 | Сombined Title | 3105-XZV-72029 | SKLPD0021-00 | 3105-XZV-72029 |  | 3104-Z-7201, 3105-Z-7244, 3105-Z-7293 | 3105-XZY-72029 | Отс. клап. 3105-P-7219A/B к 3104-MX-7201 | 3105-P-7219A/B to 3104-MX-7201 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D295/3000-S-MC-B11 | PR08 | NH-KYJYP3 24x2.5 | 385 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D295 |  |  | 3105-XZY-72029/3104-S-JB-D295 | 3000-S-SC-B01 | 3000-S-MC-B11 |  | A11 | A12 | 14 | 15 | A11-14 | A11-15 | A12-14 | A12-15 | 22 | [12 empty] | Запись в БД произведена
1725 | 3104 | Сombined Title | 3105-XZV-72029 | SKLPD0021-00 | 3105-XZV-72029 |  |  | 3105-XZZSC-72029 | Отс. клап. 3105-P-7219A/B к 3104-MX-7201 (закрыт) | 3105-P-7219A/B to 3104-MX-7201 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3105-XZZSC-72029/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 22 | [12 empty] | Запись в БД произведена
1726 | 3104 | Сombined Title | 3105-XZV-72029 | SKLPD0021-00 | 3105-XZV-72029 |  |  | 3105-XZZSO-72029 | Отс. клап. 3105-P-7219A/B к 3104-MX-7201 (открыт) | 3105-P-7219A/B to 3104-MX-7201 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7215 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C300/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 385 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C300 |  |  | 3105-XZZSO-72029/3104-S-JB-C300 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 23 | [12 empty] | Запись в БД произведена
1728 | 3105 | Сombined Title | 3105-TZIA-66362A | SAI1000-01R | 3105-TZIA-66362A |  | 3105-Z-7243 | 3105-TZT-66362A | Т подшипника 3105-P-7218A | 3105-P-7218A Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C327/3000-S-MC-B01 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 497 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C327 |  |  | 3105-TZT-66362A/3105-S-JB-C327 | 3000-S-SC-B01 | 3000-S-MC-B01 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 13 | [12 empty] | Запись в БД произведена
1729 | 2202 | 3105 | 3105-MXI-07218A | SDO0001-01 | 3105-MXI-07218A |  | 3105-Z-7227, 3105-Z-7243, 3105-Z-7292 | 3105-MXI-07218A | SIS стоп насоса упл. жидкости вакуума дегазации 3105-P-7218A | Devolatilization Vacuum Sealing Liquid Pump 3105-P-7218A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7215 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 0 | [12 empty] | Запись в БД произведена
1731 | 3105 | Сombined Title | 3105-TZIA-66362B | SAI1000-01R | 3105-TZIA-66362B |  | 3105-Z-7243 | 3105-TZT-66362B | Т подшипника 3105-P-7218B | 3105-P-7218B Bearing temperature | Temperature Transmitter | 3000_S_SC_B01 | SCS1 (SCS3->SCS1) | 2490157-3000-PR007-7215 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-TZT-66362B/3105-S-JB-C328 | 3000-S-SC-B01 | 3000-S-MC-B01 |  | A13 | A14 | 06 | - | A13-06 | - | A14-06 | - | 15 | [12 empty] | Запись в БД произведена
1732 | 2202 | 3105 | 3105-MXI-17218A | SDO0001-01 | 3105-MXI-17218A |  | 3105-Z-7227, 3105-Z-7243, 3105-Z-7292 | 3105-MXI-17218A | SIS стоп насоса упл. жидкости вакуума дегазации 3105-P-7218B | Devolatilization Vacuum Sealing Liquid Pump 3105-P-7218B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7215 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 8 | [12 empty] | Запись в БД произведена
1734 | 2202 | Сombined Title | 3105-MXI-07219A | SDO0001-01 | 3105-MXI-07219A |  | 3105-Z-7228, 3105-Z-7244, 3104-Z-7290 | 3105-MXI-07219A | SIS стоп насоса упл. жидкости вакуума преполим. 3105-P-7219A | Pre-Polymerizer Vacuum Sealing Liquid Pump 3105-P-7219A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7215 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 1 | [12 empty] | Запись в БД произведена
1736 | 2202 | Сombined Title | 3105-MXI-17219A | SDO0001-01 | 3105-MXI-17219A |  | 3105-Z-7228, 3105-Z-7244, 3104-Z-7290 | 3105-MXI-17219A | SIS стоп насоса упл. жидкости вакуума преполим. 3105-P-7219B | Pre-Polymerizer Vacuum Sealing Liquid Pump 3105-P-7219B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7215 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 9 | [12 empty] | Запись в БД произведена
1738 | 3105 | 3105 | 3105-LZSA-72036 | SDI0010-01R | 3105-LZSA-72036 |  | 3105-Z-7230 | 3105-LZS-72036 | Ур. на входе 3105-P-7217 | 3105-P-7217 Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3105-LZS-72036/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 17 | [12 empty] | Запись в БД произведена
1740 | 3105 | 3105 | 3105-LZSA-72035A | SDI0010-01R | 3105-LZSA-72035A |  | 3105-Z-7229 | 3105-LZS-72035A | Ур. на входе 3105-P-7216A | 3105-P-7216A Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C330/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 453 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C330 |  |  | 3105-LZS-72035A/3105-S-JB-C330 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 10 | [12 empty] | Запись в БД произведена
1742 | 3105 | 3105 | 3105-LZSA-72035B | SDI0010-01R | 3105-LZSA-72035B |  | 3105-Z-7229 | 3105-LZS-72035B | Ур. на входе 3105-P-7216B | 3105-P-7216B Inlet liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3105-LZS-72035B/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 16 | [12 empty] | Запись в БД произведена
1744 | 3105 | 3105 | 3105-XZV-72109 | SKLPD0021-00 | 3105-XZV-72109 |  |  | 3105-XZV-72109 | Вход 3105-P-7216AB | 3105-P-7216AB Intlet | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1745 | 3105 | 3105 | 3105-XZV-72109 | SKLPD0021-00 | 3105-XZV-72109 |  | 3105-Z-7245 | 3105-XZY-72109 | Вход 3105-P-7216AB | 3105-P-7216AB Intlet | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR05 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72109/3105-S-JB-D339 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 6 | [12 empty] | Запись в БД произведена
1746 | 3105 | 3105 | 3105-XZV-72109 | SKLPD0021-00 | 3105-XZV-72109 |  |  | 3105-XZZSC-72109 | Вход 3105-P-7216AB (закрыт) | 3105-P-7216AB Intlet | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSC-72109/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 27 | [12 empty] | Запись в БД произведена
1747 | 3105 | 3105 | 3105-XZV-72109 | SKLPD0021-00 | 3105-XZV-72109 |  |  | 3105-XZZSO-72109 | Вход 3105-P-7216AB (открыт) | 3105-P-7216AB Intlet | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSO-72109/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 0 | [12 empty] | Запись в БД произведена
1749 | 3105 | 3105 | 3105-XZV-72110 | SKLPD0021-00 | 3105-XZV-72110 |  |  | 3105-XZV-72110 | Выход 3105-P-7216AB | 3105-P-7216AB Outlet | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1750 | 3105 | 3105 | 3105-XZV-72110 | SKLPD0021-00 | 3105-XZV-72110 |  | 3105-Z-7245 | 3105-XZY-72110 | Выход 3105-P-7216AB | 3105-P-7216AB Outlet | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR06 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72110/3105-S-JB-D339 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 7 | [12 empty] | Запись в БД произведена
1751 | 3105 | 3105 | 3105-XZV-72110 | SKLPD0021-00 | 3105-XZV-72110 |  |  | 3105-XZZSC-72110 | Выход 3105-P-7216AB (закрыт) | 3105-P-7216AB Outlet | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSC-72110/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 28 | [12 empty] | Запись в БД произведена
1752 | 3105 | 3105 | 3105-XZV-72110 | SKLPD0021-00 | 3105-XZV-72110 |  |  | 3105-XZZSO-72110 | Выход 3105-P-7216AB (открыт) | 3105-P-7216AB Outlet | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSO-72110/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 1 | [12 empty] | Запись в БД произведена
1754 | 3105 | 3105 | 3105-XZV-72111 | SKLPD0021-00 | 3105-XZV-72111 |  |  | 3105-XZV-72111 | Вход 3105-P-7217 | 3105-P-7217 Intlet | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1755 | 3105 | 3105 | 3105-XZV-72111 | SKLPD0021-00 | 3105-XZV-72111 |  | 3105-Z-7246 | 3105-XZY-72111 | Вход 3105-P-7217 | 3105-P-7217 Intlet | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D339/3000-S-MC-B14 | PR07 | NH-KYJYP3 37x2.5 | 449 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D339 |  |  | 3105-XZY-72111/3105-S-JB-D339 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 8 | [12 empty] | Запись в БД произведена
1756 | 3105 | 3105 | 3105-XZV-72111 | SKLPD0021-00 | 3105-XZV-72111 |  |  | 3105-XZZSC-72111 | Вход 3105-P-7217 (закрыт) | 3105-P-7217 Intlet | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSC-72111/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 29 | [12 empty] | Запись в БД произведена
1757 | 3105 | 3105 | 3105-XZV-72111 | SKLPD0021-00 | 3105-XZV-72111 |  |  | 3105-XZZSO-72111 | Вход 3105-P-7217 (открыт) | 3105-P-7217 Intlet | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C338/3000-S-MC-B05 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 449 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C338 |  |  | 3105-XZZSO-72111/3105-S-JB-C338 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 2 | [12 empty] | Запись в БД произведена
1759 | 3105 | 3105 | 3105-XZV-72112 | SKLPD0021-00 | 3105-XZV-72112 |  |  | 3105-XZV-72112 | Выход 3105-P-7217 | 3105-P-7217 Outlet | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1760 | 3105 | 3105 | 3105-XZV-72112 | SKLPD0021-00 | 3105-XZV-72112 |  | 3105-Z-7246 | 3105-XZY-72112 | Выход 3105-P-7217 | 3105-P-7217 Outlet | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-XZY-72112/3000-S-MC-B13 |  | NH-KYJYP3 2x2.5 | 446 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B13 | Одиночный |  | 3105-XZY-72112/3000-S-MC-B13 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 17 | [12 empty] | Запись в БД произведена
1761 | 3105 | 3105 | 3105-XZV-72112 | SKLPD0021-00 | 3105-XZV-72112 |  |  | 3105-XZZSC-72112 | Выход 3105-P-7217 (закрыт) | 3105-P-7217 Outlet | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-XZZSC-72112/3000-S-MC-B05 |  | NH-IA-DJYYP3 1x2x1.5 | 446 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B05 | Одиночный |  | 3105-XZZSC-72112/3000-S-MC-B05 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 5 | [12 empty] | Запись в БД произведена
1762 | 3105 | 3105 | 3105-XZV-72112 | SKLPD0021-00 | 3105-XZV-72112 |  |  | 3105-XZZSO-72112 | Выход 3105-P-7217 (открыт) | 3105-P-7217 Outlet | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-XZZSO-72112/3000-S-MC-B05 |  | NH-IA-DJYYP3 1x2x1.5 | 446 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B05 | Одиночный |  | 3105-XZZSO-72112/3000-S-MC-B05 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 6 | [12 empty] | Запись в БД произведена
1764 | 3105 | 3105 | 3105-TZIA-66360 | SAI1000-01R | 3105-TZIA-66360 |  | 3105-Z-7246 | 3105-TZT-66360 | Т подшипника 3105-P-7217 | 3105-P-7217 Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-TZT-66360/3105-S-JB-C328 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 1 | [12 empty] | Запись в БД произведена
1765 | 2202 | 3105 | 3105-MXI-07217A | SDO0001-01 | 3105-MXI-07217A |  | 3105-Z-7230, 3105-Z-7246, 3105-Z-7292 | 3105-MXI-07217A | SIS стоп масляного насоса сепаратора 3105-P-7217 | Separator Oil Pump 3105-P-7217 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7216 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 31 | [12 empty] | Запись в БД произведена
1767 | 3105 | 3105 | 3105-TZIA-66358A | SAI1000-01R | 3105-TZIA-66358A |  | 3105-Z-7245 | 3105-TZT-66358A | Т подшипника 3105-P-7216A | 3105-P-7216A Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C327/3000-S-MC-B01 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 497 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C327 |  |  | 3105-TZT-66358A/3105-S-JB-C327 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 8 | [12 empty] | Запись в БД произведена
1768 | 2202 | 3105 | 3105-MXI-07216A | SDO0001-01 | 3105-MXI-07216A |  | 3105-Z-7229, 3105-Z-7245, 3105-Z-7292 | 3105-MXI-07216A | SIS стоп насоса откачки маслянистой воды 3105-P-7216A | Oily Water Extraction Pump 3105-P-7216A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7216 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 06 | 07 | A70-06 | A70-07 | A71-06 | A71-07 | 30 | [12 empty] | Запись в БД произведена
1770 | 3105 | 3105 | 3105-TZIA-66358B | SAI1000-01R | 3105-TZIA-66358B |  | 3105-Z-7245 | 3105-TZT-66358B | Т подшипника 3105-P-7216B | 3105-P-7216B Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7216 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 100 | 110 |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3105-S-JB-C328/3000-S-MC-B01 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 469 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C328 |  |  | 3105-TZT-66358B/3105-S-JB-C328 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 0 | [12 empty] | Запись в БД произведена
1771 | 2202 | 3105 | 3105-MXI-17216A | SDO0001-01 | 3105-MXI-17216A |  | 3105-Z-7229, 3105-Z-7245, 3105-Z-7292 | 3105-MXI-17216A | SIS стоп насоса откачки маслянистой воды 3105-P-7216B | Oily Water Extraction Pump 3105-P-7216B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7216 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 7 | [12 empty] | Запись в БД произведена
1773 | 3104 | 3104 | 3107-LZSA-74104A | SDI0010-01R | 3107-LZSA-74104A |  | 3107-Z-7411 | 3107-LZS-74104A | Ур. на входе 3107-HOP-7404A | 3107-HOP-7404A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C272/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C272 |  |  | 3107-LZS-74104A/3104-S-JB-C272 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 10 | [12 empty] | Запись в БД произведена
1775 | 3104 | 3104 | 3107-LZSA-74104B | SDI0010-01R | 3107-LZSA-74104B |  | 3107-Z-7411 | 3107-LZS-74104B | Ур. на входе 3107-HOP-7404B | 3107-HOP-7404B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3107-LZS-74104B/3104-S-JB-C274 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 16 | [12 empty] | Запись в БД произведена
1777 | 3104 | Сombined Title | 3107-XZV-74001 | SKLPD0021-00 | 3107-XZV-74001 |  |  | 3107-XZV-74001 | Отс. клап. HTF к 3107-HOP-7404 | HTF to 3107-HOP-7404 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1778 | 3104 | Сombined Title | 3107-XZV-74001 | SKLPD0021-00 | 3107-XZV-74001 |  | 3104-Z-7201 | 3107-XZY-74001 | Отс. клап. HTF к 3107-HOP-7404 | HTF to 3107-HOP-7404 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D286/3000-S-MC-B14 | PR03 | NH-KYJYP3 24x2.5 | 378 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D286 |  |  | 3107-XZY-74001/3104-S-JB-D286 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 25 | [12 empty] | Запись в БД произведена
1779 | 3104 | Сombined Title | 3107-XZV-74001 | SKLPD0021-00 | 3107-XZV-74001 |  |  | 3107-XZZSC-74001 | Отс. клап. HTF к 3107-HOP-7404 (закрыт) | HTF to 3107-HOP-7404 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3107-XZZSC-74001/3104-S-JB-C288 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 3 | [12 empty] | Запись в БД произведена
1780 | 3104 | Сombined Title | 3107-XZV-74001 | SKLPD0021-00 | 3107-XZV-74001 |  |  | 3107-XZZSO-74001 | Отс. клап. HTF к 3107-HOP-7404 (открыт) | HTF to 3107-HOP-7404 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3107-XZZSO-74001/3104-S-JB-C288 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 1 | [12 empty] | Запись в БД произведена
1782 | 3104 | Сombined Title | 3107-XZV-74002 | SKLPD0021-00 | 3107-XZV-74002 |  |  | 3107-XZV-74002 | Отс. клап. HTF к 3107-HOP-7404 | HTF to 3107-HOP-7404 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1783 | 3104 | Сombined Title | 3107-XZV-74002 | SKLPD0021-00 | 3107-XZV-74002 |  | 3104-Z-7201 | 3107-XZY-74002 | Отс. клап. HTF к 3107-HOP-7404 | HTF to 3107-HOP-7404 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D286/3000-S-MC-B14 | PR04 | NH-KYJYP3 24x2.5 | 378 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D286 |  |  | 3107-XZY-74002/3104-S-JB-D286 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 26 | [12 empty] | Запись в БД произведена
1784 | 3104 | Сombined Title | 3107-XZV-74002 | SKLPD0021-00 | 3107-XZV-74002 |  |  | 3107-XZZSC-74002 | Отс. клап. HTF к 3107-HOP-7404 (закрыт) | HTF to 3107-HOP-7404 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3107-XZZSC-74002/3104-S-JB-C288 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 0 | [12 empty] | Запись в БД произведена
1785 | 3104 | Сombined Title | 3107-XZV-74002 | SKLPD0021-00 | 3107-XZV-74002 |  |  | 3107-XZZSO-74002 | Отс. клап. HTF к 3107-HOP-7404 (открыт) | HTF to 3107-HOP-7404 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3107-XZZSO-74002/3104-S-JB-C288 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 09 | - | A11-09 | - | A12-09 | - | 2 | [12 empty] | Запись в БД произведена
1787 | 3104 | 3104 | 3107-XZV-74103 | SKLPD0021-00 | 3107-XZV-74103 |  |  | 3107-XZV-74103 | Отс. клап. на входе 3107-HOP-7404AB | 3107-HOP-7404AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1788 | 3104 | 3104 | 3107-XZV-74103 | SKLPD0021-00 | 3107-XZV-74103 |  | 3107-Z-7454 | 3107-XZY-74103 | Отс. клап. на входе 3107-HOP-7404AB | 3107-HOP-7404AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D286/3000-S-MC-B14 | PR05 | NH-KYJYP3 24x2.5 | 378 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D286 |  |  | 3107-XZY-74103/3104-S-JB-D286 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 02 | 03 | A23-02 | A23-03 | A24-02 | A24-03 | 6 | [12 empty] | Запись в БД произведена
1789 | 3104 | 3104 | 3107-XZV-74103 | SKLPD0021-00 | 3107-XZV-74103 |  |  | 3107-XZZSC-74103 | Отс. клап. на входе 3107-HOP-7404AB (закрыт) | 3107-HOP-7404AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3107-XZZSC-74103/3104-S-JB-C288 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 25 | [12 empty] | Запись в БД произведена
1790 | 3104 | 3104 | 3107-XZV-74103 | SKLPD0021-00 | 3107-XZV-74103 |  |  | 3107-XZZSO-74103 | Отс. клап. на входе 3107-HOP-7404AB (открыт) | 3107-HOP-7404AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3107-XZZSO-74103/3104-S-JB-C288 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 27 | [12 empty] | Запись в БД произведена
1792 | 3104 | 3104 | 3107-XZV-74104 | SKLPD0021-00 | 3107-XZV-74104 |  |  | 3107-XZV-74104 | Отс. клап. на выходе 3107-HOP-7404AB | 3107-HOP-7404AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1793 | 3104 | 3104 | 3107-XZV-74104 | SKLPD0021-00 | 3107-XZV-74104 |  | 3107-Z-7454 | 3107-XZY-74104 | Отс. клап. на выходе 3107-HOP-7404AB | 3107-HOP-7404AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D286/3000-S-MC-B14 | PR06 | NH-KYJYP3 24x2.5 | 378 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D286 |  |  | 3107-XZY-74104/3104-S-JB-D286 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 02 | 03 | A23-02 | A23-03 | A24-02 | A24-03 | 7 | [12 empty] | Запись в БД произведена
1794 | 3104 | 3104 | 3107-XZV-74104 | SKLPD0021-00 | 3107-XZV-74104 |  |  | 3107-XZZSC-74104 | Отс. клап. на выходе 3107-HOP-7404AB (закрыт) | 3107-HOP-7404AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3107-XZZSC-74104/3104-S-JB-C288 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 26 | [12 empty] | Запись в БД произведена
1795 | 3104 | 3104 | 3107-XZV-74104 | SKLPD0021-00 | 3107-XZV-74104 |  |  | 3107-XZZSO-74104 | Отс. клап. на выходе 3107-HOP-7404AB (открыт) | 3107-HOP-7404AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7402 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C288/3000-S-MC-B07 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 434 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C288 |  |  | 3107-XZZSO-74104/3104-S-JB-C288 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 28 | [12 empty] | Запись в БД произведена
1797 | 2202 | 3104 | 3107-MXI-47404A | SDO0001-01 | 3107-MXI-47404A |  | 3107-Z-7411, 3107-Z-7454, 3104-Z-7290 | 3107-MXI-47404A | SIS стоп насоса HTF подогревателя сырья 3107-HOP-7404A | Feedstock Preheater HTF Pump 3107-HOP-7404A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 25 | [12 empty] | Запись в БД произведена
1799 | 2202 | 3104 | 3107-MXI-57404A | SDO0001-01 | 3107-MXI-57404A |  | 3107-Z-7411, 3107-Z-7454, 3104-Z-7290 | 3107-MXI-57404A | SIS стоп насоса HTF подогревателя сырья 3107-HOP-7404B | Feedstock Preheater HTF Pump 3107-HOP-7404B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7402 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 16 | [12 empty] | Запись в БД произведена
1801 | 3104 | 3104 | 3107-LZSA-74105A | SDI0010-01R | 3107-LZSA-74105A |  | 3107-Z-7412 | 3107-LZS-74105A | Ур. на входе 3107-HOP-7405A | 3107-HOP-7405A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C254/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 427 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C254 |  |  | 3107-LZS-74105A/3104-S-JB-C254 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 0 | [12 empty] | Запись в БД произведена
1803 | 3104 | 3104 | 3107-LZSA-74105B | SDI0010-01R | 3107-LZSA-74105B |  | 3107-Z-7412 | 3107-LZS-74105B | Ур. на входе 3107-HOP-7405B | 3107-HOP-7405B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C255/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C255 |  |  | 3107-LZS-74105B/3104-S-JB-C255 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 5 | [12 empty] | Запись в БД произведена
1805 | 3104 | 3104 | 3107-LZSA-74106A | SDI0010-01R | 3107-LZSA-74106A |  | 3107-Z-7413 | 3107-LZS-74106A | Ур. на входе 3107-HOP-7406A | 3107-HOP-7406A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C254/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 427 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C254 |  |  | 3107-LZS-74106A/3104-S-JB-C254 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 1 | [12 empty] | Запись в БД произведена
1807 | 3104 | 3104 | 3107-LZSA-74106B | SDI0010-01R | 3107-LZSA-74106B |  | 3107-Z-7413 | 3107-LZS-74106B | Ур. на входе 3107-HOP-7406B | 3107-HOP-7406B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C255/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C255 |  |  | 3107-LZS-74106B/3104-S-JB-C255 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 6 | [12 empty] | Запись в БД произведена
1809 | 3104 | Сombined Title | 3107-XZV-74003 | SKLPD0021-00 | 3107-XZV-74003 |  |  | 3107-XZV-74003 | Отс. клап. HTF к 3107-HOP-7406 | HTF to 3107-HOP-7406 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1810 | 3104 | Сombined Title | 3107-XZV-74003 | SKLPD0021-00 | 3107-XZV-74003 |  | 3104-Z-7207 | 3107-XZY-74003 | Отс. клап. HTF к 3107-HOP-7406 | HTF to 3107-HOP-7406 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR05 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3107-XZY-74003/3104-S-JB-D263 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 15 | [12 empty] | Запись в БД произведена
1811 | 3104 | Сombined Title | 3107-XZV-74003 | SKLPD0021-00 | 3107-XZV-74003 |  |  | 3107-XZZSC-74003 | Отс. клап. HTF к 3107-HOP-7406 (закрыт) | HTF to 3107-HOP-7406 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSC-74003/3104-S-JB-C273 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 16 | [12 empty] | Запись в БД произведена
1812 | 3104 | Сombined Title | 3107-XZV-74003 | SKLPD0021-00 | 3107-XZV-74003 |  |  | 3107-XZZSO-74003 | Отс. клап. HTF к 3107-HOP-7406 (открыт) | HTF to 3107-HOP-7406 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSO-74003/3104-S-JB-C273 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 20 | [12 empty] | Запись в БД произведена
1814 | 3104 | Сombined Title | 3107-XZV-74004 | SKLPD0021-00 | 3107-XZV-74004 |  |  | 3107-XZV-74004 | Отс. клап. HTF к 3107-HOP-7406 | HTF to 3107-HOP-7406 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1815 | 3104 | Сombined Title | 3107-XZV-74004 | SKLPD0021-00 | 3107-XZV-74004 |  | 3104-Z-7207 | 3107-XZY-74004 | Отс. клап. HTF к 3107-HOP-7406 | HTF to 3107-HOP-7406 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR06 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3107-XZY-74004/3104-S-JB-D263 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 16 | [12 empty] | Запись в БД произведена
1816 | 3104 | Сombined Title | 3107-XZV-74004 | SKLPD0021-00 | 3107-XZV-74004 |  |  | 3107-XZZSC-74004 | Отс. клап. HTF к 3107-HOP-7406 (закрыт) | HTF to 3107-HOP-7406 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSC-74004/3104-S-JB-C273 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 17 | [12 empty] | Запись в БД произведена
1817 | 3104 | Сombined Title | 3107-XZV-74004 | SKLPD0021-00 | 3107-XZV-74004 |  |  | 3107-XZZSO-74004 | Отс. клап. HTF к 3107-HOP-7406 (открыт) | HTF to 3107-HOP-7406 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSO-74004/3104-S-JB-C273 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 21 | [12 empty] | Запись в БД произведена
1819 | 3104 | Сombined Title | 3107-XZV-74005 | SKLPD0021-00 | 3107-XZV-74005 |  |  | 3107-XZV-74005 | Отс. клап. HTF к 3107-HOP-7405 | HTF to 3107-HOP-7405 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1820 | 3104 | Сombined Title | 3107-XZV-74005 | SKLPD0021-00 | 3107-XZV-74005 |  | 3104-Z-7202 | 3107-XZY-74005 | Отс. клап. HTF к 3107-HOP-7405 | HTF to 3107-HOP-7405 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR07 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3107-XZY-74005/3104-S-JB-D263 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 17 | [12 empty] | Запись в БД произведена
1821 | 3104 | Сombined Title | 3107-XZV-74005 | SKLPD0021-00 | 3107-XZV-74005 |  |  | 3107-XZZSC-74005 | Отс. клап. HTF к 3107-HOP-7405 (закрыт) | HTF to 3107-HOP-7405 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSC-74005/3104-S-JB-C273 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 18 | [12 empty] | Запись в БД произведена
1822 | 3104 | Сombined Title | 3107-XZV-74005 | SKLPD0021-00 | 3107-XZV-74005 |  |  | 3107-XZZSO-74005 | Отс. клап. HTF к 3107-HOP-7405 (открыт) | HTF to 3107-HOP-7405 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSO-74005/3104-S-JB-C273 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 22 | [12 empty] | Запись в БД произведена
1824 | 3104 | Сombined Title | 3107-XZV-74006 | SKLPD0021-00 | 3107-XZV-74006 |  |  | 3107-XZV-74006 | Отс. клап. HTF к 3107-HOP-7405 | HTF to 3107-HOP-7405 cut-off valve | On-Off Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1825 | 3104 | Сombined Title | 3107-XZV-74006 | SKLPD0021-00 | 3107-XZV-74006 |  | 3104-Z-7202 | 3107-XZY-74006 | Отс. клап. HTF к 3107-HOP-7405 | HTF to 3107-HOP-7405 cut-off valve | Solenoid Valve | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR08 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3107-XZY-74006/3104-S-JB-D263 | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 18 | [12 empty] | Запись в БД произведена
1826 | 3104 | Сombined Title | 3107-XZV-74006 | SKLPD0021-00 | 3107-XZV-74006 |  |  | 3107-XZZSC-74006 | Отс. клап. HTF к 3107-HOP-7405 (закрыт) | HTF to 3107-HOP-7405 cut-off valve | Limit Switch - Close | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSC-74006/3104-S-JB-C273 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 19 | [12 empty] | Запись в БД произведена
1827 | 3104 | Сombined Title | 3107-XZV-74006 | SKLPD0021-00 | 3107-XZV-74006 |  |  | 3107-XZZSO-74006 | Отс. клап. HTF к 3107-HOP-7405 (открыт) | HTF to 3107-HOP-7405 cut-off valve | Limit Switch - Open | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSO-74006/3104-S-JB-C273 | 3000-S-SC-B01 | 3000-S-MC-B07 |  | A11 | A12 | 08 | - | A11-08 | - | A12-08 | - | 23 | [12 empty] | Запись в БД произведена
1829 | 3104 | 3104 | 3107-XZV-74105 | SKLPD0021-00 | 3107-XZV-74105 |  |  | 3107-XZV-74105 | Отс. клап. на входе 3107-HOP-7405AB | 3107-HOP-7405AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1830 | 3104 | 3104 | 3107-XZV-74105 | SKLPD0021-00 | 3107-XZV-74105 |  | 3107-Z-7455 | 3107-XZY-74105 | Отс. клап. на входе 3107-HOP-7405AB | 3107-HOP-7405AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR09 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3107-XZY-74105/3104-S-JB-D263 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 22 | [12 empty] | Запись в БД произведена
1831 | 3104 | 3104 | 3107-XZV-74105 | SKLPD0021-00 | 3107-XZV-74105 |  |  | 3107-XZZSC-74105 | Отс. клап. на входе 3107-HOP-7405AB (закрыт) | 3107-HOP-7405AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSC-74105/3104-S-JB-C273 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 12 | [12 empty] | Запись в БД произведена
1832 | 3104 | 3104 | 3107-XZV-74105 | SKLPD0021-00 | 3107-XZV-74105 |  |  | 3107-XZZSO-74105 | Отс. клап. на входе 3107-HOP-7405AB (открыт) | 3107-HOP-7405AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSO-74105/3104-S-JB-C273 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 15 | [12 empty] | Запись в БД произведена
1834 | 3104 | 3104 | 3107-XZV-74106 | SKLPD0021-00 | 3107-XZV-74106 |  |  | 3107-XZV-74106 | Отс. клап. на выходе 3107-HOP-7405AB | 3107-HOP-7405AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1835 | 3104 | 3104 | 3107-XZV-74106 | SKLPD0021-00 | 3107-XZV-74106 |  | 3107-Z-7455 | 3107-XZY-74106 | Отс. клап. на выходе 3107-HOP-7405AB | 3107-HOP-7405AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR10 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3107-XZY-74106/3104-S-JB-D263 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 23 | [12 empty] | Запись в БД произведена
1836 | 3104 | 3104 | 3107-XZV-74106 | SKLPD0021-00 | 3107-XZV-74106 |  |  | 3107-XZZSC-74106 | Отс. клап. на выходе 3107-HOP-7405AB (закрыт) | 3107-HOP-7405AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSC-74106/3104-S-JB-C273 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 13 | [12 empty] | Запись в БД произведена
1837 | 3104 | 3104 | 3107-XZV-74106 | SKLPD0021-00 | 3107-XZV-74106 |  |  | 3107-XZZSO-74106 | Отс. клап. на выходе 3107-HOP-7405AB (открыт) | 3107-HOP-7405AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C272/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 436 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C272 |  |  | 3107-XZZSO-74106/3104-S-JB-C272 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 11 | [12 empty] | Запись в БД произведена
1839 | 3104 | 3104 | 3107-XZV-74107 | SKLPD0021-00 | 3107-XZV-74107 |  |  | 3107-XZV-74107 | Отс. клап. на входе 3107-HOP-7406AB | 3107-HOP-7406AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1840 | 3104 | 3104 | 3107-XZV-74107 | SKLPD0021-00 | 3107-XZV-74107 |  | 3107-Z-7456 | 3107-XZY-74107 | Отс. клап. на входе 3107-HOP-7406AB | 3107-HOP-7406AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR11 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3107-XZY-74107/3104-S-JB-D263 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 24 | [12 empty] | Запись в БД произведена
1841 | 3104 | 3104 | 3107-XZV-74107 | SKLPD0021-00 | 3107-XZV-74107 |  |  | 3107-XZZSC-74107 | Отс. клап. на входе 3107-HOP-7406AB (закрыт) | 3107-HOP-7406AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C273/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C273 |  |  | 3107-XZZSC-74107/3104-S-JB-C273 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 14 | [12 empty] | Запись в БД произведена
1842 | 3104 | 3104 | 3107-XZV-74107 | SKLPD0021-00 | 3107-XZV-74107 |  |  | 3107-XZZSO-74107 | Отс. клап. на входе 3107-HOP-7406AB (открыт) | 3107-HOP-7406AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSO-74107/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 13 | [12 empty] | Запись в БД произведена
1844 | 3104 | 3104 | 3107-XZV-74108 | SKLPD0021-00 | 3107-XZV-74108 |  |  | 3107-XZV-74108 | Отс. клап. на выходе 3107-HOP-7406AB | 3107-HOP-7406AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1845 | 3104 | 3104 | 3107-XZV-74108 | SKLPD0021-00 | 3107-XZV-74108 |  | 3107-Z-7456 | 3107-XZY-74108 | Отс. клап. на выходе 3107-HOP-7406AB | 3107-HOP-7406AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR01 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74108/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 27 | [12 empty] | Запись в БД произведена
1846 | 3104 | 3104 | 3107-XZV-74108 | SKLPD0021-00 | 3107-XZV-74108 |  |  | 3107-XZZSC-74108 | Отс. клап. на выходе 3107-HOP-7406AB (закрыт) | 3107-HOP-7406AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3107-XZZSC-74108/3104-S-JB-C274 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 17 | [12 empty] | Запись в БД произведена
1847 | 3104 | 3104 | 3107-XZV-74108 | SKLPD0021-00 | 3107-XZV-74108 |  |  | 3107-XZZSO-74108 | Отс. клап. на выходе 3107-HOP-7406AB (открыт) | 3107-HOP-7406AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7403 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3107-XZZSO-74108/3104-S-JB-C274 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 22 | [12 empty] | Запись в БД произведена
1849 | 2202 | 3104 | 3107-MXI-47405A | SDO0001-01 | 3107-MXI-47405A |  | 3107-Z-7412, 3107-Z-7455, 3104-Z-7290 | 3107-MXI-47405A | SIS стоп насоса HTF первого преполим. 3107-HOP-7405A | First Pre-Polymerizer HTF Pump 3107-HOP-7405A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7403 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 26 | [12 empty] | Запись в БД произведена
1851 | 2202 | 3104 | 3107-MXI-57405A | SDO0001-01 | 3107-MXI-57405A |  | 3107-Z-7412, 3107-Z-7455, 3104-Z-7290 | 3107-MXI-57405A | SIS стоп насоса HTF первого преполим. 3107-HOP-7405B | First Pre-Polymerizer HTF Pump 3107-HOP-7405B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7403 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 17 | [12 empty] | Запись в БД произведена
1853 | 2202 | 3104 | 3107-MXI-47406A | SDO0001-01 | 3107-MXI-47406A |  | 3107-Z-7413, 3107-Z-7456, 3104-Z-7290 | 3107-MXI-47406A | SIS стоп насоса HTF второго преполим. 3107-HOP-7406A | Second Pre-Polymerizer HTF Pump 3107-HOP-7406A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7403 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 27 | [12 empty] | Запись в БД произведена
1855 | 2202 | 3104 | 3107-MXI-57406A | SDO0001-01 | 3107-MXI-57406A |  | 3107-Z-7413, 3107-Z-7456, 3104-Z-7290 | 3107-MXI-57406A | SIS стоп насоса HTF второго преполим. 3107-HOP-7406B | Second Pre-Polymerizer HTF Pump 3107-HOP-7406B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7403 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 18 | [12 empty] | Запись в БД произведена
1857 | 3104 | 3104 | 3107-LZSA-74107A | SDI0010-01R | 3107-LZSA-74107A |  | 3107-Z-7414 | 3107-LZS-74107A | Ур. на входе 3107-HOP-7407A | 3107-HOP-7407A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C254/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 427 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C254 |  |  | 3107-LZS-74107A/3104-S-JB-C254 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 2 | [12 empty] | Запись в БД произведена
1859 | 3104 | 3104 | 3107-LZSA-74107B | SDI0010-01R | 3107-LZSA-74107B |  | 3107-Z-7414 | 3107-LZS-74107B | Ур. на входе 3107-HOP-7407B | 3107-HOP-7407B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C255/3000-S-MC-B07 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C255 |  |  | 3107-LZS-74107B/3104-S-JB-C255 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 7 | [12 empty] | Запись в БД произведена
1861 | 3104 | 3104 | 3107-LZSA-74107C | SDI0010-01R | 3107-LZSA-74107C |  | 3107-Z-7414 | 3107-LZS-74107C | Ур. на входе 3107-HOP-7407C | 3107-HOP-7407C Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C255/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C255 |  |  | 3107-LZS-74107C/3104-S-JB-C255 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 8 | [12 empty] | Запись в БД произведена
1863 | 3104 | 3104 | 3107-XZV-74109 | SKLPD0021-00 | 3107-XZV-74109 |  |  | 3107-XZV-74109 | Отс. клап. на входе 3107-HOP-7407AB | 3107-HOP-7407AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1864 | 3104 | 3104 | 3107-XZV-74109 | SKLPD0021-00 | 3107-XZV-74109 |  | 3107-Z-7457 | 3107-XZY-74109 | Отс. клап. на входе 3107-HOP-7407AB | 3107-HOP-7407AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR02 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74109/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 28 | [12 empty] | Запись в БД произведена
1865 | 3104 | 3104 | 3107-XZV-74109 | SKLPD0021-00 | 3107-XZV-74109 |  |  | 3107-XZZSC-74109 | Отс. клап. на входе 3107-HOP-7407AB (закрыт) | 3107-HOP-7407AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3107-XZZSC-74109/3104-S-JB-C274 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 18 | [12 empty] | Запись в БД произведена
1866 | 3104 | 3104 | 3107-XZV-74109 | SKLPD0021-00 | 3107-XZV-74109 |  |  | 3107-XZZSO-74109 | Отс. клап. на входе 3107-HOP-7407AB (открыт) | 3107-HOP-7407AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3107-XZZSO-74109/3104-S-JB-C274 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 23 | [12 empty] | Запись в БД произведена
1868 | 3104 | 3104 | 3107-XZV-74110 | SKLPD0021-00 | 3107-XZV-74110 |  |  | 3107-XZV-74110 | Отс. клап. на выходе 3107-HOP-7407AB | 3107-HOP-7407AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1869 | 3104 | 3104 | 3107-XZV-74110 | SKLPD0021-00 | 3107-XZV-74110 |  | 3107-Z-7457 | 3107-XZY-74110 | Отс. клап. на выходе 3107-HOP-7407AB | 3107-HOP-7407AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR08 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74110/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 29 | [12 empty] | Запись в БД произведена
1870 | 3104 | 3104 | 3107-XZV-74110 | SKLPD0021-00 | 3107-XZV-74110 |  |  | 3107-XZZSC-74110 | Отс. клап. на выходе 3107-HOP-7407AB (закрыт) | 3107-HOP-7407AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSC-74110/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 9 | [12 empty] | Запись в БД произведена
1871 | 3104 | 3104 | 3107-XZV-74110 | SKLPD0021-00 | 3107-XZV-74110 |  |  | 3107-XZZSO-74110 | Отс. клап. на выходе 3107-HOP-7407AB (открыт) | 3107-HOP-7407AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSO-74110/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 14 | [12 empty] | Запись в БД произведена
1873 | 3104 | 3104 | 3107-XZV-74111 | SKLPD0021-00 | 3107-XZV-74111 |  |  | 3107-XZV-74111 | Отс. клап. на входе 3107-HOP-7407C | 3107-HOP-7407C Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1874 | 3104 | 3104 | 3107-XZV-74111 | SKLPD0021-00 | 3107-XZV-74111 |  | 3107-Z-7467 | 3107-XZY-74111 | Отс. клап. на входе 3107-HOP-7407C | 3107-HOP-7407C Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR04 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74111/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 30 | [12 empty] | Запись в БД произведена
1875 | 3104 | 3104 | 3107-XZV-74111 | SKLPD0021-00 | 3107-XZV-74111 |  |  | 3107-XZZSC-74111 | Отс. клап. на входе 3107-HOP-7407C (закрыт) | 3107-HOP-7407C Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3107-XZZSC-74111/3104-S-JB-C274 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 19 | [12 empty] | Запись в БД произведена
1876 | 3104 | 3104 | 3107-XZV-74111 | SKLPD0021-00 | 3107-XZV-74111 |  |  | 3107-XZZSO-74111 | Отс. клап. на входе 3107-HOP-7407C (открыт) | 3107-HOP-7407C Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3107-XZZSO-74111/3104-S-JB-C274 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 24 | [12 empty] | Запись в БД произведена
1878 | 3104 | 3104 | 3107-XZV-74112 | SKLPD0021-00 | 3107-XZV-74112 |  |  | 3107-XZV-74112 | Отс. клап. на выходе 3107-HOP-7407C | 3107-HOP-7407C Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1879 | 3104 | 3104 | 3107-XZV-74112 | SKLPD0021-00 | 3107-XZV-74112 |  | 3107-Z-7467 | 3107-XZY-74112 | Отс. клап. на выходе 3107-HOP-7407C | 3107-HOP-7407C Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR09 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74112/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 31 | [12 empty] | Запись в БД произведена
1880 | 3104 | 3104 | 3107-XZV-74112 | SKLPD0021-00 | 3107-XZV-74112 |  |  | 3107-XZZSC-74112 | Отс. клап. на выходе 3107-HOP-7407C (закрыт) | 3107-HOP-7407C Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSC-74112/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 10 | [12 empty] | Запись в БД произведена
1881 | 3104 | 3104 | 3107-XZV-74112 | SKLPD0021-00 | 3107-XZV-74112 |  |  | 3107-XZZSO-74112 | Отс. клап. на выходе 3107-HOP-7407C (открыт) | 3107-HOP-7407C Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7404 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSO-74112/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 15 | [12 empty] | Запись в БД произведена
1883 | 2202 | 3104 | 3107-MXI-47407A | SDO0001-01 | 3107-MXI-47407A |  | 3107-Z-7414, 3107-Z-7457, 3104-Z-7290 | 3107-MXI-47407A | SIS стоп насоса HTF первого полимеризатора 3107-HOP-7407A | First Polymerizer HTF Pump 3107-HOP-7407A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7404 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 28 | [12 empty] | Запись в БД произведена
1885 | 2202 | 3104 | 3107-MXI-57407A | SDO0001-01 | 3107-MXI-57407A |  | 3107-Z-7414, 3107-Z-7457, 3107-Z-7467, 3104-Z-7290 | 3107-MXI-57407A | SIS стоп насоса HTF первого полимеризатора 3107-HOP-7407B | First Polymerizer HTF Pump 3107-HOP-7407B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7404 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 19 | [12 empty] | Запись в БД произведена
1887 | 2202 | 3104 | 3107-MXI-67407A | SDO0001-01 | 3107-MXI-67407A |  | 3107-Z-7414, 3107-Z-7467, 3104-Z-7290 | 3107-MXI-67407A | SIS стоп насоса HTF первого полимеризатора 3107-HOP-7407C | First Polymerizer HTF Pump 3107-HOP-7407C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7404 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 0 | [12 empty] | Запись в БД произведена
1889 | 3104 | 3104 | 3107-LZSA-74108A | SDI0010-01R | 3107-LZSA-74108A |  | 3107-Z-7415 | 3107-LZS-74108A | Ур. на входе 3107-HOP-7408A | 3107-HOP-7408A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C254/3000-S-MC-B07 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 427 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C254 |  |  | 3107-LZS-74108A/3104-S-JB-C254 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 3 | [12 empty] | Запись в БД произведена
1891 | 3104 | 3104 | 3107-LZSA-74108B | SDI0010-01R | 3107-LZSA-74108B |  | 3107-Z-7415 | 3107-LZS-74108B | Ур. на входе 3107-HOP-7408B | 3107-HOP-7408B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C255/3000-S-MC-B07 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C255 |  |  | 3107-LZS-74108B/3104-S-JB-C255 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 9 | [12 empty] | Запись в БД произведена
1893 | 3104 | 3104 | 3107-LZSA-74108C | SDI0010-01R | 3107-LZSA-74108C |  | 3107-Z-7415 | 3107-LZS-74108C | Ур. на входе 3107-HOP-7408C | 3107-HOP-7408C Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C254/3000-S-MC-B07 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 427 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C254 |  |  | 3107-LZS-74108C/3104-S-JB-C254 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 4 | [12 empty] | Запись в БД произведена
1895 | 3104 | 3104 | 3107-XZV-74113 | SKLPD0021-00 | 3107-XZV-74113 |  |  | 3107-XZV-74113 | Отс. клап. на входе 3107-HOP-7408AB | 3107-HOP-7408AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1896 | 3104 | 3104 | 3107-XZV-74113 | SKLPD0021-00 | 3107-XZV-74113 |  | 3107-Z-7458 | 3107-XZY-74113 | Отс. клап. на входе 3107-HOP-7408AB | 3107-HOP-7408AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR05 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74113/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 02 | 03 | A23-02 | A23-03 | A24-02 | A24-03 | 0 | [12 empty] | Запись в БД произведена
1897 | 3104 | 3104 | 3107-XZV-74113 | SKLPD0021-00 | 3107-XZV-74113 |  |  | 3107-XZZSC-74113 | Отс. клап. на входе 3107-HOP-7408AB (закрыт) | 3107-HOP-7408AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3107-XZZSC-74113/3104-S-JB-C274 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 20 | [12 empty] | Запись в БД произведена
1898 | 3104 | 3104 | 3107-XZV-74113 | SKLPD0021-00 | 3107-XZV-74113 |  |  | 3107-XZZSO-74113 | Отс. клап. на входе 3107-HOP-7408AB (открыт) | 3107-HOP-7408AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSO-74113/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 16 | [12 empty] | Запись в БД произведена
1900 | 3104 | 3104 | 3107-XZV-74114 | SKLPD0021-00 | 3107-XZV-74114 |  |  | 3107-XZV-74114 | Отс. клап. на выходе 3107-HOP-7408AB | 3107-HOP-7408AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1901 | 3104 | 3104 | 3107-XZV-74114 | SKLPD0021-00 | 3107-XZV-74114 |  | 3107-Z-7458 | 3107-XZY-74114 | Отс. клап. на выходе 3107-HOP-7408AB | 3107-HOP-7408AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR10 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74114/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 02 | 03 | A23-02 | A23-03 | A24-02 | A24-03 | 1 | [12 empty] | Запись в БД произведена
1902 | 3104 | 3104 | 3107-XZV-74114 | SKLPD0021-00 | 3107-XZV-74114 |  |  | 3107-XZZSC-74114 | Отс. клап. на выходе 3107-HOP-7408AB (закрыт) | 3107-HOP-7408AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C271/3000-S-MC-B08 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 411 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C271 |  |  | 3107-XZZSC-74114/3104-S-JB-C271 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 0 | [12 empty] | Запись в БД произведена
1903 | 3104 | 3104 | 3107-XZV-74114 | SKLPD0021-00 | 3107-XZV-74114 |  |  | 3107-XZZSO-74114 | Отс. клап. на выходе 3107-HOP-7408AB (открыт) | 3107-HOP-7408AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C271/3000-S-MC-B08 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 411 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C271 |  |  | 3107-XZZSO-74114/3104-S-JB-C271 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 4 | [12 empty] | Запись в БД произведена
1905 | 3104 | 3104 | 3107-XZV-74115 | SKLPD0021-00 | 3107-XZV-74115 |  |  | 3107-XZV-74115 | Отс. клап. на входе 3107-HOP-7408C | 3107-HOP-7408C Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1906 | 3104 | 3104 | 3107-XZV-74115 | SKLPD0021-00 | 3107-XZV-74115 |  | 3107-Z-7468 | 3107-XZY-74115 | Отс. клап. на входе 3107-HOP-7408C | 3107-HOP-7408C Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR06 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74115/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 02 | 03 | A23-02 | A23-03 | A24-02 | A24-03 | 2 | [12 empty] | Запись в БД произведена
1907 | 3104 | 3104 | 3107-XZV-74115 | SKLPD0021-00 | 3107-XZV-74115 |  |  | 3107-XZZSC-74115 | Отс. клап. на входе 3107-HOP-7408C (закрыт) | 3107-HOP-7408C Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C274/3000-S-MC-B07 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 436 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C274 |  |  | 3107-XZZSC-74115/3104-S-JB-C274 | 3000-S-SC-B02 | 3000-S-MC-B07 |  | A21 | A22 | 12 | - | A21-12 | - | A22-12 | - | 21 | [12 empty] | Запись в БД произведена
1908 | 3104 | 3104 | 3107-XZV-74115 | SKLPD0021-00 | 3107-XZV-74115 |  |  | 3107-XZZSO-74115 | Отс. клап. на входе 3107-HOP-7408C (открыт) | 3107-HOP-7408C Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C271/3000-S-MC-B08 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 411 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C271 |  |  | 3107-XZZSO-74115/3104-S-JB-C271 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 5 | [12 empty] | Запись в БД произведена
1910 | 3104 | 3104 | 3107-XZV-74116 | SKLPD0021-00 | 3107-XZV-74116 |  |  | 3107-XZV-74116 | Отс. клап. на выходе 3107-HOP-7408C | 3107-HOP-7408C Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1911 | 3104 | 3104 | 3107-XZV-74116 | SKLPD0021-00 | 3107-XZV-74116 |  | 3107-Z-7468 | 3107-XZY-74116 | Отс. клап. на выходе 3107-HOP-7408C | 3107-HOP-7408C Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR11 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74116/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 02 | 03 | A23-02 | A23-03 | A24-02 | A24-03 | 3 | [12 empty] | Запись в БД произведена
1912 | 3104 | 3104 | 3107-XZV-74116 | SKLPD0021-00 | 3107-XZV-74116 |  |  | 3107-XZZSC-74116 | Отс. клап. на выходе 3107-HOP-7408C (закрыт) | 3107-HOP-7408C Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C271/3000-S-MC-B08 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 411 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C271 |  |  | 3107-XZZSC-74116/3104-S-JB-C271 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 1 | [12 empty] | Запись в БД произведена
1913 | 3104 | 3104 | 3107-XZV-74116 | SKLPD0021-00 | 3107-XZV-74116 |  |  | 3107-XZZSO-74116 | Отс. клап. на выходе 3107-HOP-7408C (открыт) | 3107-HOP-7408C Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7405 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C271/3000-S-MC-B08 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 411 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C271 |  |  | 3107-XZZSO-74116/3104-S-JB-C271 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 6 | [12 empty] | Запись в БД произведена
1915 | 2202 | 3104 | 3107-MXI-47408A | SDO0001-01 | 3107-MXI-47408A |  | 3107-Z-7415, 3107-Z-7458, 3104-Z-7290 | 3107-MXI-47408A | SIS стоп насоса HTF второго полимеризатора 3107-HOP-7408A | Second Polymerizer HTF Pump 3107-HOP-7408A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7405 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 29 | [12 empty] | Запись в БД произведена
1917 | 2202 | 3104 | 3107-MXI-57408A | SDO0001-01 | 3107-MXI-57408A |  | 3107-Z-7415, 3107-Z-7458, 3107-Z-7468, 3104-Z-7290 | 3107-MXI-57408A | SIS стоп насоса HTF второго полимеризатора 3107-HOP-7408B | Second Polymerizer HTF Pump 3107-HOP-7408B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7405 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 20 | [12 empty] | Запись в БД произведена
1919 | 2202 | 3104 | 3107-MXI-67408A | SDO0001-01 | 3107-MXI-67408A |  | 3107-Z-7415, 3107-Z-7468, 3104-Z-7290 | 3107-MXI-67408A | SIS стоп насоса HTF второго полимеризатора 3107-HOP-7408C | Second Polymerizer HTF Pump 3107-HOP-7408C SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7405 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 1 | [12 empty] | Запись в БД произведена
1921 | 3104 | 3104 | 3107-LZSA-74109 | SDI0010-01R | 3107-LZSA-74109 |  | 3107-Z-7416 | 3107-LZS-74109 | Ур. на входе 3107-HOP-7409 | 3107-HOP-7409 Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C250/3000-S-MC-B06 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 425 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C250 |  |  | 3107-LZS-74109/3104-S-JB-C250 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 26 | [12 empty] | Запись в БД произведена
1923 | 3104 | 3104 | 3107-LZSA-74110A | SDI0010-01R | 3107-LZSA-74110A |  | 3107-Z-7417 | 3107-LZS-74110A | Ур. на входе 3107-HOP-7410A | 3107-HOP-7410A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C250/3000-S-MC-B06 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 425 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C250 |  |  | 3107-LZS-74110A/3104-S-JB-C250 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 27 | [12 empty] | Запись в БД произведена
1925 | 3104 | 3104 | 3107-LZSA-74110B | SDI0010-01R | 3107-LZSA-74110B |  | 3107-Z-7417 | 3107-LZS-74110B | Ур. на входе 3107-HOP-7410B | 3107-HOP-7410B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C250/3000-S-MC-B06 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 425 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C250 |  |  | 3107-LZS-74110B/3104-S-JB-C250 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 28 | [12 empty] | Запись в БД произведена
1927 | 3104 | 3104 | 3107-XZV-74117 | SKLPD0021-00 | 3107-XZV-74117 |  |  | 3107-XZV-74117 | Отс. клап. на входе 3107-HOP-7409 | 3107-HOP-7409 Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1928 | 3104 | 3104 | 3107-XZV-74117 | SKLPD0021-00 | 3107-XZV-74117 |  | 3107-Z-7459 | 3107-XZY-74117 | Отс. клап. на входе 3107-HOP-7409 | 3107-HOP-7409 Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR07 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74117/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 02 | 03 | A23-02 | A23-03 | A24-02 | A24-03 | 4 | [12 empty] | Запись в БД произведена
1929 | 3104 | 3104 | 3107-XZV-74117 | SKLPD0021-00 | 3107-XZV-74117 |  |  | 3107-XZZSC-74117 | Отс. клап. на входе 3107-HOP-7409 (закрыт) | 3107-HOP-7409 Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C271/3000-S-MC-B08 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 411 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C271 |  |  | 3107-XZZSC-74117/3104-S-JB-C271 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 2 | [12 empty] | Запись в БД произведена
1930 | 3104 | 3104 | 3107-XZV-74117 | SKLPD0021-00 | 3107-XZV-74117 |  |  | 3107-XZZSO-74117 | Отс. клап. на входе 3107-HOP-7409 (открыт) | 3107-HOP-7409 Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C271/3000-S-MC-B08 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 411 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C271 |  |  | 3107-XZZSO-74117/3104-S-JB-C271 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 7 | [12 empty] | Запись в БД произведена
1932 | 3104 | 3104 | 3107-XZV-74118 | SKLPD0021-00 | 3107-XZV-74118 |  |  | 3107-XZV-74118 | Отс. клап. на выходе 3107-HOP-7409 | 3107-HOP-7409 Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1933 | 3104 | 3104 | 3107-XZV-74118 | SKLPD0021-00 | 3107-XZV-74118 |  | 3107-Z-7459 | 3107-XZY-74118 | Отс. клап. на выходе 3107-HOP-7409 | 3107-HOP-7409 Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D264/3000-S-MC-B14 | PR12 | NH-KYJYP3 37x2.5 | 433 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D264 |  |  | 3107-XZY-74118/3104-S-JB-D264 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 02 | 03 | A23-02 | A23-03 | A24-02 | A24-03 | 5 | [12 empty] | Запись в БД произведена
1934 | 3104 | 3104 | 3107-XZV-74118 | SKLPD0021-00 | 3107-XZV-74118 |  |  | 3107-XZZSC-74118 | Отс. клап. на выходе 3107-HOP-7409 (закрыт) | 3107-HOP-7409 Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSC-74118/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 11 | [12 empty] | Запись в БД произведена
1935 | 3104 | 3104 | 3107-XZV-74118 | SKLPD0021-00 | 3107-XZV-74118 |  |  | 3107-XZZSO-74118 | Отс. клап. на выходе 3107-HOP-7409 (открыт) | 3107-HOP-7409 Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSO-74118/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 17 | [12 empty] | Запись в БД произведена
1937 | 3104 | 3104 | 3107-XZV-74119 | SKLPD0021-00 | 3107-XZV-74119 |  |  | 3107-XZV-74119 | Отс. клап. на входе 3107-HOP-7410AB | 3107-HOP-7410AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1938 | 3104 | 3104 | 3107-XZV-74119 | SKLPD0021-00 | 3107-XZV-74119 |  | 3107-Z-7460 | 3107-XZY-74119 | Отс. клап. на входе 3107-HOP-7410AB | 3107-HOP-7410AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR03 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3107-XZY-74119/3104-S-JB-D263 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 25 | [12 empty] | Запись в БД произведена
1939 | 3104 | 3104 | 3107-XZV-74119 | SKLPD0021-00 | 3107-XZV-74119 |  |  | 3107-XZZSC-74119 | Отс. клап. на входе 3107-HOP-7410AB (закрыт) | 3107-HOP-7410AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C271/3000-S-MC-B08 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 411 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C271 |  |  | 3107-XZZSC-74119/3104-S-JB-C271 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 3 | [12 empty] | Запись в БД произведена
1940 | 3104 | 3104 | 3107-XZV-74119 | SKLPD0021-00 | 3107-XZV-74119 |  |  | 3107-XZZSO-74119 | Отс. клап. на входе 3107-HOP-7410AB (открыт) | 3107-HOP-7410AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C271/3000-S-MC-B08 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 411 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C271 |  |  | 3107-XZZSO-74119/3104-S-JB-C271 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 8 | [12 empty] | Запись в БД произведена
1942 | 3104 | 3104 | 3107-XZV-74120 | SKLPD0021-00 | 3107-XZV-74120 |  |  | 3107-XZV-74120 | Отс. клап. на выходе 3107-HOP-7410AB | 3107-HOP-7410AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1943 | 3104 | 3104 | 3107-XZV-74120 | SKLPD0021-00 | 3107-XZV-74120 |  | 3107-Z-7460 | 3107-XZY-74120 | Отс. клап. на выходе 3107-HOP-7410AB | 3107-HOP-7410AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-D263/3000-S-MC-B12 | PR04 | NH-KYJYP3 37x2.5 | 438 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3104-S-JB-D263 |  |  | 3107-XZY-74120/3104-S-JB-D263 | 3000-S-SC-B02 | 3000-S-MC-B12 |  | A23 | A24 | 00 | 01 | A23-00 | A23-01 | A24-00 | A24-01 | 26 | [12 empty] | Запись в БД произведена
1944 | 3104 | 3104 | 3107-XZV-74120 | SKLPD0021-00 | 3107-XZV-74120 |  |  | 3107-XZZSC-74120 | Отс. клап. на выходе 3107-HOP-7410AB (закрыт) | 3107-HOP-7410AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSC-74120/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 12 | [12 empty] | Запись в БД произведена
1945 | 3104 | 3104 | 3107-XZV-74120 | SKLPD0021-00 | 3107-XZV-74120 |  |  | 3107-XZZSO-74120 | Отс. клап. на выходе 3107-HOP-7410AB (открыт) | 3107-HOP-7410AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR007-7406 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3104-S-JB-C275/3000-S-MC-B08 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 431 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C275 |  |  | 3107-XZZSO-74120/3104-S-JB-C275 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 18 | [12 empty] | Запись в БД произведена
1947 | 2202 | 3104 | 3107-MXI-47409A | SDO0001-01 | 3107-MXI-47409A |  | 3107-Z-7416,3107-Z-7459, 3104-Z-7290 | 3107-MXI-47409A | SIS стоп верхнего насоса HTF третьего полимеризатора 3107-HOP-7409 | Third Polymerizer Upper HTF Pump 3107-HOP-7409 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7406 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 30 | [12 empty] | Запись в БД произведена
1949 | 2202 | 3104 | 3107-MXI-47410A | SDO0001-01 | 3107-MXI-47410A |  | 3107-Z-7417, 3107-Z-7460, 3104-Z-7290 | 3107-MXI-47410A | SIS стоп нижнего насоса HTF третьего полимеризатора 3107-HOP-7410A | Third Polymerizer Lower HTF Pump 3107-HOP-7410A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7406 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 08 | 09 | A70-08 | A70-09 | A71-08 | A71-09 | 31 | [12 empty] | Запись в БД произведена
1951 | 2202 | 3104 | 3107-MXI-57410A | SDO0001-01 | 3107-MXI-57410A |  | 3107-Z-7417, 3107-Z-7459, 3107-Z-7460, 3104-Z-7290 | 3107-MXI-57410A | SIS стоп нижнего насоса HTF третьего полимеризатора 3107-HOP-7410B | Third Polymerizer Lower HTF Pump 3107-HOP-7410B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7406 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 21 | [12 empty] | Запись в БД произведена
1953 | 3105 | 3105 | 3107-LZSA-74011A | SDI0010-01R | 3107-LZSA-74011A |  | 3107-Z-7418 | 3107-LZS-74011A | Ур. на входе 3107-HOP-7411A | 3107-HOP-7411A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C324/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C324 |  |  | 3107-LZS-74011A/3105-S-JB-C324 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 28 | [12 empty] | Запись в БД произведена
1955 | 3105 | 3105 | 3107-LZSA-74011B | SDI0010-01R | 3107-LZSA-74011B |  | 3107-Z-7418 | 3107-LZS-74011B | Ур. на входе 3107-HOP-7411B | 3107-HOP-7411B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C323/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C323 |  |  | 3107-LZS-74011B/3105-S-JB-C323 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 22 | [12 empty] | Запись в БД произведена
1957 | 3105 | 3105 | 3107-XZV-74121 | SKLPD0021-00 | 3107-XZV-74121 |  |  | 3107-XZV-74121 | Отс. клап. на входе 3107-HOP-7411AB | 3107-HOP-7411AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1958 | 3105 | 3105 | 3107-XZV-74121 | SKLPD0021-00 | 3107-XZV-74121 |  | 3107-Z-7461 | 3107-XZY-74121 | Отс. клап. на входе 3107-HOP-7411AB | 3107-HOP-7411AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR02 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74121/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 26 | [12 empty] | Запись в БД произведена
1959 | 3105 | 3105 | 3107-XZV-74121 | SKLPD0021-00 | 3107-XZV-74121 |  |  | 3107-XZZSC-74121 | Отс. клап. на входе 3107-HOP-7411AB (закрыт) | 3107-HOP-7411AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C330/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 453 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C330 |  |  | 3107-XZZSC-74121/3105-S-JB-C330 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 12 | [12 empty] | Запись в БД произведена
1960 | 3105 | 3105 | 3107-XZV-74121 | SKLPD0021-00 | 3107-XZV-74121 |  |  | 3107-XZZSO-74121 | Отс. клап. на входе 3107-HOP-7411AB (открыт) | 3107-HOP-7411AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C330/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 453 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C330 |  |  | 3107-XZZSO-74121/3105-S-JB-C330 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 14 | [12 empty] | Запись в БД произведена
1962 | 3105 | 3105 | 3107-XZV-74122 | SKLPD0021-00 | 3107-XZV-74122 |  |  | 3107-XZV-74122 | Отс. клап. на выходе 3107-HOP-7411AB | 3107-HOP-7411AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1963 | 3105 | 3105 | 3107-XZV-74122 | SKLPD0021-00 | 3107-XZV-74122 |  | 3107-Z-7461 | 3107-XZY-74122 | Отс. клап. на выходе 3107-HOP-7411AB | 3107-HOP-7411AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR03 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74122/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 27 | [12 empty] | Запись в БД произведена
1964 | 3105 | 3105 | 3107-XZV-74122 | SKLPD0021-00 | 3107-XZV-74122 |  |  | 3107-XZZSC-74122 | Отс. клап. на выходе 3107-HOP-7411AB (закрыт) | 3107-HOP-7411AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C330/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 453 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C330 |  |  | 3107-XZZSC-74122/3105-S-JB-C330 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 13 | [12 empty] | Запись в БД произведена
1965 | 3105 | 3105 | 3107-XZV-74122 | SKLPD0021-00 | 3107-XZV-74122 |  |  | 3107-XZZSO-74122 | Отс. клап. на выходе 3107-HOP-7411AB (открыт) | 3107-HOP-7411AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7407 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C330/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 453 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C330 |  |  | 3107-XZZSO-74122/3105-S-JB-C330 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 15 | [12 empty] | Запись в БД произведена
1967 | 2202 | 3105 | 3107-MXI-47411A | SDO0001-01 | 3107-MXI-47411A |  | 3107-Z-7418, 3107-Z-7461, 3105-Z-7292 | 3107-MXI-47411A | SIS стоп насоса HTF подогревателя дегазации 3107-HOP-7411A | Devolatilization Heater HTF Pump 3107-HOP-7411A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7407 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 0 | [12 empty] | Запись в БД произведена
1969 | 2202 | 3105 | 3107-MXI-57411A | SDO0001-01 | 3107-MXI-57411A |  | 3107-Z-7418, 3107-Z-7461, 3105-Z-7292 | 3107-MXI-57411A | SIS стоп насоса HTF подогревателя дегазации 3107-HOP-7411B | Devolatilization Heater HTF Pump 3107-HOP-7411B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7407 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 22 | [12 empty] | Запись в БД произведена
1971 | 3105 | 3105 | 3107-LZSA-74012A | SDI0010-01R | 3107-LZSA-74012A |  | 3107-Z-7419 | 3107-LZS-74012A | Ур. на входе 3107-HOP-7412A | 3107-HOP-7412A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C324/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C324 |  |  | 3107-LZS-74012A/3105-S-JB-C324 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 29 | [12 empty] | Запись в БД произведена
1973 | 3105 | 3105 | 3107-LZSA-74012B | SDI0010-01R | 3107-LZSA-74012B |  | 3107-Z-7419 | 3107-LZS-74012B | Ур. на входе 3107-HOP-7412B | 3107-HOP-7412B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C323/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C323 |  |  | 3107-LZS-74012B/3105-S-JB-C323 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 23 | [12 empty] | Запись в БД произведена
1975 | 3105 | 3105 | 3107-LZSA-74013A | SDI0010-01R | 3107-LZSA-74013A |  | 3107-Z-7420 | 3107-LZS-74013A | Ур. на входе 3107-HOP-7413A | 3107-HOP-7413A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C324/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C324 |  |  | 3107-LZS-74013A/3105-S-JB-C324 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 30 | [12 empty] | Запись в БД произведена
1977 | 3105 | 3105 | 3107-LZSA-74013B | SDI0010-01R | 3107-LZSA-74013B |  | 3107-Z-7420 | 3107-LZS-74013B | Ур. на входе 3107-HOP-7413B | 3107-HOP-7413B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C323/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C323 |  |  | 3107-LZS-74013B/3105-S-JB-C323 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 24 | [12 empty] | Запись в БД произведена
1979 | 3105 | 3105 | 3107-XZV-74123 | SKLPD0021-00 | 3107-XZV-74123 |  |  | 3107-XZV-74123 | Отс. клап. на входе 3107-HOP-7412AB | 3107-HOP-7412AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1980 | 3105 | 3105 | 3107-XZV-74123 | SKLPD0021-00 | 3107-XZV-74123 |  | 3107-Z-7462 | 3107-XZY-74123 | Отс. клап. на входе 3107-HOP-7412AB | 3107-HOP-7412AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR04 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74123/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 28 | [12 empty] | Запись в БД произведена
1981 | 3105 | 3105 | 3107-XZV-74123 | SKLPD0021-00 | 3107-XZV-74123 |  |  | 3107-XZZSC-74123 | Отс. клап. на входе 3107-HOP-7412AB (закрыт) | 3107-HOP-7412AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3107-XZZSC-74123/3105-S-JB-C329 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 0 | [12 empty] | Запись в БД произведена
1982 | 3105 | 3105 | 3107-XZV-74123 | SKLPD0021-00 | 3107-XZV-74123 |  |  | 3107-XZZSO-74123 | Отс. клап. на входе 3107-HOP-7412AB (открыт) | 3107-HOP-7412AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3107-XZZSO-74123/3105-S-JB-C329 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 4 | [12 empty] | Запись в БД произведена
1984 | 3105 | 3105 | 3107-XZV-74124 | SKLPD0021-00 | 3107-XZV-74124 |  |  | 3107-XZV-74124 | Отс. клап. на выходе 3107-HOP-7412AB | 3107-HOP-7412AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1985 | 3105 | 3105 | 3107-XZV-74124 | SKLPD0021-00 | 3107-XZV-74124 |  | 3107-Z-7462 | 3107-XZY-74124 | Отс. клап. на выходе 3107-HOP-7412AB | 3107-HOP-7412AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR05 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74124/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 29 | [12 empty] | Запись в БД произведена
1986 | 3105 | 3105 | 3107-XZV-74124 | SKLPD0021-00 | 3107-XZV-74124 |  |  | 3107-XZZSC-74124 | Отс. клап. на выходе 3107-HOP-7412AB (закрыт) | 3107-HOP-7412AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3107-XZZSC-74124/3105-S-JB-C329 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 1 | [12 empty] | Запись в БД произведена
1987 | 3105 | 3105 | 3107-XZV-74124 | SKLPD0021-00 | 3107-XZV-74124 |  |  | 3107-XZZSO-74124 | Отс. клап. на выходе 3107-HOP-7412AB (открыт) | 3107-HOP-7412AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3107-XZZSO-74124/3105-S-JB-C329 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 5 | [12 empty] | Запись в БД произведена
1989 | 3105 | 3105 | 3107-XZV-74125 | SKLPD0021-00 | 3107-XZV-74125 |  |  | 3107-XZV-74125 | Отс. клап. на входе 3107-HOP-7413AB | 3107-HOP-7413AB Inlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1990 | 3105 | 3105 | 3107-XZV-74125 | SKLPD0021-00 | 3107-XZV-74125 |  | 3107-Z-7463 | 3107-XZY-74125 | Отс. клап. на входе 3107-HOP-7413AB | 3107-HOP-7413AB Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR06 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74125/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 30 | [12 empty] | Запись в БД произведена
1991 | 3105 | 3105 | 3107-XZV-74125 | SKLPD0021-00 | 3107-XZV-74125 |  |  | 3107-XZZSC-74125 | Отс. клап. на входе 3107-HOP-7413AB (закрыт) | 3107-HOP-7413AB Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3107-XZZSC-74125/3105-S-JB-C329 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 2 | [12 empty] | Запись в БД произведена
1992 | 3105 | 3105 | 3107-XZV-74125 | SKLPD0021-00 | 3107-XZV-74125 |  |  | 3107-XZZSO-74125 | Отс. клап. на входе 3107-HOP-7413AB (открыт) | 3107-HOP-7413AB Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3107-XZZSO-74125/3105-S-JB-C329 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 6 | [12 empty] | Запись в БД произведена
1994 | 3105 | 3105 | 3107-XZV-74126 | SKLPD0021-00 | 3107-XZV-74126 |  |  | 3107-XZV-74126 | Отс. клап. на выходе 3107-HOP-7413AB | 3107-HOP-7413AB Outlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
1995 | 3105 | 3105 | 3107-XZV-74126 | SKLPD0021-00 | 3107-XZV-74126 |  | 3107-Z-7463 | 3107-XZY-74126 | Отс. клап. на выходе 3107-HOP-7413AB | 3107-HOP-7413AB Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR07 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74126/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 12 | [12 empty] | Запись в БД произведена
1996 | 3105 | 3105 | 3107-XZV-74126 | SKLPD0021-00 | 3107-XZV-74126 |  |  | 3107-XZZSC-74126 | Отс. клап. на выходе 3107-HOP-7413AB (закрыт) | 3107-HOP-7413AB Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3107-XZZSC-74126/3105-S-JB-C329 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 3 | [12 empty] | Запись в БД произведена
1997 | 3105 | 3105 | 3107-XZV-74126 | SKLPD0021-00 | 3107-XZV-74126 |  |  | 3107-XZZSO-74126 | Отс. клап. на выходе 3107-HOP-7413AB (открыт) | 3107-HOP-7413AB Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7408 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C329/3000-S-MC-B05 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 474 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C329 |  |  | 3107-XZZSO-74126/3105-S-JB-C329 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 7 | [12 empty] | Запись в БД произведена
1999 | 2202 | 3105 | 3107-MXI-47412A | SDO0001-01 | 3107-MXI-47412A |  | 3107-Z-7419, 3107-Z-7462, 3105-Z-7292 | 3107-MXI-47412A | SIS стоп насоса HTF системы основной дегазации 3107-HOP-7412A | Main Devolatilization System HTF Pump 3107-HOP-7412A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7408 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 1 | [12 empty] | Запись в БД произведена
2001 | 2202 | 3105 | 3107-MXI-57412A | SDO0001-01 | 3107-MXI-57412A |  | 3107-Z-7419, 3107-Z-7462, 3105-Z-7292 | 3107-MXI-57412A | SIS стоп насоса HTF системы основной дегазации 3107-HOP-7412B | Main Devolatilization System HTF Pump 3107-HOP-7412B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7408 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 23 | [12 empty] | Запись в БД произведена
2003 | 2202 | 3105 | 3107-MXI-47413A | SDO0001-01 | 3107-MXI-47413A |  | 3107-Z-7420, 3107-Z-7463, 3105-Z-7292 | 3107-MXI-47413A | SIS стоп насоса HTF системы финальной дегазации 3107-HOP-7413A | Final Devolatilization System HTF Pump 3107-HOP-7413A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7408 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 2 | [12 empty] | Запись в БД произведена
2005 | 2202 | 3105 | 3107-MXI-57413A | SDO0001-01 | 3107-MXI-57413A |  | 3107-Z-7420, 3107-Z-7463, 3105-Z-7292 | 3107-MXI-57413A | SIS стоп насоса HTF системы финальной дегазации 3107-HOP-7413B | Final Devolatilization System HTF Pump 3107-HOP-7413B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7408 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 24 | [12 empty] | Запись в БД произведена
2007 | 3105 | 3105 | 3107-LZSA-74014A | SDI0010-01R | 3107-LZSA-74014A |  | 3107-Z-7422 | 3107-LZS-74014A | Ур. на входе 3107-HOP-7414A | 3107-HOP-7414A Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C324/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C324 |  |  | 3107-LZS-74014A/3105-S-JB-C324 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 31 | [12 empty] | Запись в БД произведена
2009 | 3105 | 3105 | 3107-LZSA-74014B | SDI0010-01R | 3107-LZSA-74014B |  | 3107-Z-7422 | 3107-LZS-74014B | Ур. на входе 3107-HOP-7414B | 3107-HOP-7414B Inlet Liquid level indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C323/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 480 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C323 |  |  | 3107-LZS-74014B/3105-S-JB-C323 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 25 | [12 empty] | Запись в БД произведена
2011 | 3105 | 3105 | 3107-XZV-74127 | SKLPD0021-00 | 3107-XZV-74127 |  |  | 3107-XZV-74127 | Отс. клап. на входе 3107-HOP-7414A | 3107-HOP-7414A Inlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
2012 | 3105 | 3105 | 3107-XZV-74127 | SKLPD0021-00 | 3107-XZV-74127 |  | 3107-Z-7464 | 3107-XZY-74127 | Отс. клап. на входе 3107-HOP-7414A | 3107-HOP-7414A Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR08 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74127/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 13 | [12 empty] | Запись в БД произведена
2013 | 3105 | 3105 | 3107-XZV-74127 | SKLPD0021-00 | 3107-XZV-74127 |  |  | 3107-XZZSC-74127 | Отс. клап. на входе 3107-HOP-7414A (закрыт) | 3107-HOP-7414A Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3107-XZZSC-74127/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 19 | [12 empty] | Запись в БД произведена
2014 | 3105 | 3105 | 3107-XZV-74127 | SKLPD0021-00 | 3107-XZV-74127 |  |  | 3107-XZZSO-74127 | Отс. клап. на входе 3107-HOP-7414A (открыт) | 3107-HOP-7414A Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3107-XZZSO-74127/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 23 | [12 empty] | Запись в БД произведена
2016 | 3105 | 3105 | 3107-XZV-74128 | SKLPD0021-00 | 3107-XZV-74128 |  |  | 3107-XZV-74128 | Отс. клап. на выходе 3107-HOP-7414A | 3107-HOP-7414A Outlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
2017 | 3105 | 3105 | 3107-XZV-74128 | SKLPD0021-00 | 3107-XZV-74128 |  | 3107-Z-7464 | 3107-XZY-74128 | Отс. клап. на выходе 3107-HOP-7414A | 3107-HOP-7414A Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR09 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74128/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 14 | [12 empty] | Запись в БД произведена
2018 | 3105 | 3105 | 3107-XZV-74128 | SKLPD0021-00 | 3107-XZV-74128 |  |  | 3107-XZZSC-74128 | Отс. клап. на выходе 3107-HOP-7414A (закрыт) | 3107-HOP-7414A Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3107-XZZSC-74128/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 20 | [12 empty] | Запись в БД произведена
2019 | 3105 | 3105 | 3107-XZV-74128 | SKLPD0021-00 | 3107-XZV-74128 |  |  | 3107-XZZSO-74128 | Отс. клап. на выходе 3107-HOP-7414A (открыт) | 3107-HOP-7414A Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3107-XZZSO-74128/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 24 | [12 empty] | Запись в БД произведена
2021 | 3105 | 3105 | 3107-XZV-74129 | SKLPD0021-00 | 3107-XZV-74129 |  |  | 3107-XZV-74129 | Отс. клап. на входе 3107-HOP-7414B | 3107-HOP-7414B Inlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
2022 | 3105 | 3105 | 3107-XZV-74129 | SKLPD0021-00 | 3107-XZV-74129 |  | 3107-Z-7465 | 3107-XZY-74129 | Отс. клап. на входе 3107-HOP-7414B | 3107-HOP-7414B Inlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR10 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74129/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 15 | [12 empty] | Запись в БД произведена
2023 | 3105 | 3105 | 3107-XZV-74129 | SKLPD0021-00 | 3107-XZV-74129 |  |  | 3107-XZZSC-74129 | Отс. клап. на входе 3107-HOP-7414B (закрыт) | 3107-HOP-7414B Inlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3107-XZZSC-74129/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 21 | [12 empty] | Запись в БД произведена
2024 | 3105 | 3105 | 3107-XZV-74129 | SKLPD0021-00 | 3107-XZV-74129 |  |  | 3107-XZZSO-74129 | Отс. клап. на входе 3107-HOP-7414B (открыт) | 3107-HOP-7414B Inlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3107-XZZSO-74129/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 25 | [12 empty] | Запись в БД произведена
2026 | 3105 | 3105 | 3107-XZV-74130 | SKLPD0021-00 | 3107-XZV-74130 |  |  | 3107-XZV-74130 | Отс. клап. на выходе 3107-HOP-7414B | 3107-HOP-7414B Outlet cutoff valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
2027 | 3105 | 3105 | 3107-XZV-74130 | SKLPD0021-00 | 3107-XZV-74130 |  | 3107-Z-7465 | 3107-XZY-74130 | Отс. клап. на выходе 3107-HOP-7414B | 3107-HOP-7414B Outlet cutoff valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-D332/3000-S-MC-B10 | PR11 | NH-KYJYP3 37x2.5 | 469 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3105-S-JB-D332 |  |  | 3107-XZY-74130/3105-S-JB-D332 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 16 | [12 empty] | Запись в БД произведена
2028 | 3105 | 3105 | 3107-XZV-74130 | SKLPD0021-00 | 3107-XZV-74130 |  |  | 3107-XZZSC-74130 | Отс. клап. на выходе 3107-HOP-7414B (закрыт) | 3107-HOP-7414B Outlet cutoff valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3107-XZZSC-74130/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 22 | [12 empty] | Запись в БД произведена
2029 | 3105 | 3105 | 3107-XZV-74130 | SKLPD0021-00 | 3107-XZV-74130 |  |  | 3107-XZZSO-74130 | Отс. клап. на выходе 3107-HOP-7414B (открыт) | 3107-HOP-7414B Outlet cutoff valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7409 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3105-S-JB-C331/3000-S-MC-B05 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 497 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3105-S-JB-C331 |  |  | 3107-XZZSO-74130/3105-S-JB-C331 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 08 | - | A31-08 | - | A32-08 | - | 26 | [12 empty] | Запись в БД произведена
2031 | 2202 | 3105 | 3107-MXI-47414A | SDO0001-01 | 3107-MXI-47414A |  | 3107-Z-7464, 3105-Z-7292, 3107-Z-7422 | 3107-MXI-47414A | SIS стоп насоса HTF теплообменника расплава 3107-HOP-7414A | Melt Heat Exchanger HTF Pump 3107-HOP-7414A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7409 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S04 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 3 | [12 empty] | Запись в БД произведена
2033 | 2202 | 3105 | 3107-MXI-57414A | SDO0001-01 | 3107-MXI-57414A |  | 3107-Z-7465, 3105-Z-7292, 3107-Z-7422 | 3107-MXI-57414A | SIS стоп насоса HTF теплообменника расплава 3107-HOP-7414B | Melt Heat Exchanger HTF Pump 3107-HOP-7414B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7409 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 10 | 11 | A70-10 | A70-11 | A71-10 | A71-11 | 25 | [12 empty] | Запись в БД произведена
2035 | 3107 |  | 3107-XZV-74009 | SKLPD0021-00 | 3107-XZV-74009 |  |  | 3107-XZV-74009 | Отс. клап. печи горячего масла | Hot Oil Furnace Shut-off Valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
2036 | 3107 | 3107 | 3107-XZV-74009 | SKLPD0021-00 | 3107-XZV-74009 |  | 3107-Z-7466, 3107-Z-6499 | 3107-XZY-74009 | Отс. клап. печи горячего масла | Hot Oil Furnace Shut-off Valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-D407/3000-S-MC-B13 | PR04 | NH-KYJYP3 16x2.5 | 447 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D407 |  |  | 3107-XZY-74009/3107-S-JB-D407 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 2 | [12 empty] | Запись в БД произведена
2037 | 3107 | 3107 | 3107-XZV-74009 | SKLPD0021-00 | 3107-XZV-74009 |  |  | 3107-XZZSC-74009 | Отс. клап. печи горячего масла (закрыт) | Hot Oil Furnace Shut-off Valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSC-74009/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 3 | [12 empty] | Запись в БД произведена
2038 | 3107 | 3107 | 3107-XZV-74009 | SKLPD0021-00 | 3107-XZV-74009 |  |  | 3107-XZZSO-74009 | Отс. клап. печи горячего масла (открыт) | Hot Oil Furnace Shut-off Valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSO-74009/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 9 | [12 empty] | Запись в БД произведена
2040 | 3107 |  | 3107-XZV-74010 | SKLPD0021-00 | 3107-XZV-74010 |  |  | 3107-XZV-74010 | Азот к 3107-HF-7401 | Nitrogen to 3107-HF-7401 | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
2041 | 3107 | 3107 | 3107-XZV-74010 | SKLPD0021-00 | 3107-XZV-74010 |  | 3107-Z-7466 | 3107-XZY-74010 | Азот к 3107-HF-7401 | Nitrogen to 3107-HF-7401 | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-D407/3000-S-MC-B13 | PR06 | NH-KYJYP3 16x2.5 | 447 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D407 |  |  | 3107-XZY-74010/3107-S-JB-D407 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 3 | [12 empty] | Запись в БД произведена
2042 | 3107 | 3107 | 3107-XZV-74010 | SKLPD0021-00 | 3107-XZV-74010 |  |  | 3107-XZZSC-74010 | Азот к 3107-HF-7401 (закрыт) | Nitrogen to 3107-HF-7401 | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSC-74010/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 4 | [12 empty] | Запись в БД произведена
2043 | 3107 | 3107 | 3107-XZV-74010 | SKLPD0021-00 | 3107-XZV-74010 |  |  | 3107-XZZSO-74010 | Азот к 3107-HF-7401 (открыт) | Nitrogen to 3107-HF-7401 | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C401/3000-S-MC-B08 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 449 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C401 |  |  | 3107-XZZSO-74010/3107-S-JB-C401 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 13 | - | A31-13 | - | A32-13 | - | 10 | [12 empty] | Запись в БД произведена
2045 | 3107 |  | 3107-XZV-74011 | SKLPD0021-00 | 3107-XZV-74011 |  |  | 3107-XZV-74011 | Дренаж теплоносителя из 3107-HF-7401 | Heat transfer oil drain from 3107-HF-7401 | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field |  |  | SIS | [15 empty] | REV 3 | NEW |  | ИД 2026 07 03
2046 | 3107 | 3107 | 3107-XZV-74011 | SKLPD0021-00 | 3107-XZV-74011 |  | 3107-Z-7466 | 3107-XZY-74011 | Дренаж теплоносителя из 3107-HF-7401 | Heat transfer oil drain from 3107-HF-7401 | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-D407/3000-S-MC-B13 | PR03 | NH-KYJYP3 16x2.5 | 447 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D407 |  |  | 3107-XZY-74011/3107-S-JB-D407 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 4 | [12 empty] | Запись в БД произведена
2047 | 3107 | 3107 | 3107-XZV-74011 | SKLPD0021-00 | 3107-XZV-74011 |  |  | 3107-XZZSC-74011 | Дренаж теплоносителя из 3107-HF-7401 (закрыт) | Heat transfer oil drain from 3107-HF-7401 | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C404/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 447 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C404 |  |  | 3107-XZZSC-74011/3107-S-JB-C404 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 9 | [12 empty] | Запись в БД произведена
2048 | 3107 | 3107 | 3107-XZV-74011 | SKLPD0021-00 | 3107-XZV-74011 |  |  | 3107-XZZSO-74011 | Дренаж теплоносителя из 3107-HF-7401 (открыт) | Heat transfer oil drain from 3107-HF-7401 | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3107-S-JB-C404/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 447 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C404 |  |  | 3107-XZZSO-74011/3107-S-JB-C404 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 10 | [12 empty] | Запись в БД произведена
2050 | 3107 | 3107 | 3107-TZIA-74503A | SAI1000-01R | 3107-TZIA-74503A |  | new 3107-Z-7491, 3107-Z-7493 | 3107-TZT-74503A | Т теплоносителя на выходе (Блок.) | Heat transfer oil outlet temperature(Interlock) | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C771/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C771 |  |  | 3107-TZT-74503A/3107-S-JB-C771 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 7 | [12 empty] | Запись в БД произведена
2051 | 3107 | 3107 | 3107-TZIA-74503B | SAI1000-01R | 3107-TZIA-74503B |  | new 3107-Z-7491, 3107-Z-7493 | 3107-TZT-74503B | Т теплоносителя на выходе (Блок.) | Heat transfer oil outlet temperature(Interlock) | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C772/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C772 |  |  | 3107-TZT-74503B/3107-S-JB-C772 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 14 | [12 empty] | Запись в БД произведена
2052 | 3107 | 3107 | 3107-TZIA-74503C | SAI1000-01R | 3107-TZIA-74503C |  | new 3107-Z-7491, 3107-Z-7493 | 3107-TZT-74503C | Т теплоносителя на выходе (Блок.) | Heat transfer oil outlet temperature(Interlock) | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C773/3000-S-MC-B01 | PR01 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C773 |  |  | 3107-TZT-74503C/3107-S-JB-C773 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 5 | [12 empty] | Запись в БД произведена
2054 | 3107 | 3107 | 3107-TZIA-74505A | SAI1000-01R | 3107-TZIA-74505A |  | new 3107-Z-7491, 3107-Z-7493, 3107-Z-7497 | 3107-TZT-74505A | Т дымовых газов на выходе печи | Furnace outlet exhaust temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 340 | 370 |  | ℃ |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C771/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C771 |  |  | 3107-TZT-74505A/3107-S-JB-C771 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 8 | [12 empty] | Запись в БД произведена
2055 | 3107 | 3107 | 3107-TZIA-74505B | SAI1000-01R | 3107-TZIA-74505B |  | new 3107-Z-7491, 3107-Z-7493, 3107-Z-7497 | 3107-TZT-74505B | Т дымовых газов на выходе печи | Furnace outlet exhaust temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 340 | 370 |  | ℃ |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C772/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C772 |  |  | 3107-TZT-74505B/3107-S-JB-C772 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 0 | [12 empty] | Запись в БД произведена
2056 | 3107 | 3107 | 3107-TZIA-74505C | SAI1000-01R | 3107-TZIA-74505C |  | new 3107-Z-7491, 3107-Z-7493, 3107-Z-7497 | 3107-TZT-74505C | Т дымовых газов на выходе печи | Furnace outlet exhaust temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 340 | 370 |  | ℃ |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C773/3000-S-MC-B01 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C773 |  |  | 3107-TZT-74505C/3107-S-JB-C773 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 6 | [12 empty] | Запись в БД произведена
2058 | 3107 | 3107 | 3107-PZIA-74502A | SAI1000-01R | 3107-PZIA-74502A |  | new 3107-Z-7491, 3107-Z-7496 | 3107-PZT-74502A | Р ПГ перед горелкой | NG Pressure before entering the burner | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 260 | kPaG | 0 | 260 | kPaG | 2 | 3 | 105 | 115 |  | kPaG |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C771/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C771 |  |  | 3107-PZT-74502A/3107-S-JB-C771 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 4 | [12 empty] | Запись в БД произведена
2059 | 3107 | 3107 | 3107-PZIA-74502B | SAI1000-01R | 3107-PZIA-74502B |  | new 3107-Z-7491, 3107-Z-7496 | 3107-PZT-74502B | Р ПГ перед горелкой | NG Pressure before entering the burner | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 260 | kPaG | 0 | 260 | kPaG | 2 | 3 | 105 | 115 |  | kPaG |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C772/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C772 |  |  | 3107-PZT-74502B/3107-S-JB-C772 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 11 | [12 empty] | Запись в БД произведена
2060 | 3107 | 3107 | 3107-PZIA-74502C | SAI1000-01R | 3107-PZIA-74502C |  | new3107-Z-7491, 3107-Z-7496 | 3107-PZT-74502C | Р ПГ перед горелкой | NG Pressure before entering the burner | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 260 | kPaG | 0 | 260 | kPaG | 2 | 3 | 105 | 115 |  | kPaG |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C773/3000-S-MC-B01 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C773 |  |  | 3107-PZT-74502C/3107-S-JB-C773 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 3 | [12 empty] | Запись в БД произведена
2062 | 3107 | 3107 | [5 empty] | 3107-FZE-74503A | Расход теплоносителя | Heat transfer oil flow | Measure Orifice |  |  | 2490157-3000-PR007-7401 | Field |  |  | SIS | [17 empty] | 3107-PK-7401 | ИД 2026 07 03
2063 | 3107 | 3107 | 3107-FZIA-74503A | SAI1000-01R | 3107-FZIA-74503A |  | new 3107-Z-7491 | 3107-FZT-74503A | Расход теплоносителя | Heat transfer oil flow | D/P Flow Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 300 | m3/h | 0 | 300 | m3/h | 145 | 155 |  |  |  | m3/h |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C771/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C771 |  |  | 3107-FZT-74503A/3107-S-JB-C771 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 3 | [12 empty] | Запись в БД произведена
2064 | 3107 | 3107 | 3107-FZIA-74503B | SAI1000-01R | 3107-FZIA-74503B |  | new 3107-Z-7491 | 3107-FZT-74503B | Расход теплоносителя | Heat transfer oil flow | D/P Flow Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 300 | m3/h | 0 | 300 | m3/h | 145 | 155 |  |  |  | m3/h |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C772/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C772 |  |  | 3107-FZT-74503B/3107-S-JB-C772 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 10 | [12 empty] | Запись в БД произведена
2065 | 3107 | 3107 | 3107-FZIA-74503C | SAI1000-01R | 3107-FZIA-74503C |  | new 3107-Z-7491 | 3107-FZT-74503C | Расход теплоносителя | Heat transfer oil flow | D/P Flow Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 300 | m3/h | 0 | 300 | m3/h | 145 | 155 |  |  |  | m3/h |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C773/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C773 |  |  | 3107-FZT-74503C/3107-S-JB-C773 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 2 | [12 empty] | Запись в БД произведена
2067 | 3107 | 3107 | 3107-PZIA-74506A | SAI1000-01R | 3107-PZIA-74506A |  | 3107-Z-7466, 3107-Z-7491, 3107-Z-7497 | 3107-PZT-74506A | Р на выходе печи теплоносителя | Outlet pressure of thermal oil furnace | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 1,2 | MPaG | 0 | 1,2 | MPaG | 0.3 | 0.35 |  |  |  | MPaG |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C771/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C771 |  |  | 3107-PZT-74506A/3107-S-JB-C771 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 6 | [12 empty] | Запись в БД произведена
2068 | 3107 | 3107 | 3107-PZIA-74506B | SAI1000-01R | 3107-PZIA-74506B |  | 3107-Z-7466, 3107-Z-7491, 3107-Z-7497 | 3107-PZT-74506B | Р на выходе печи теплоносителя | Outlet pressure of thermal oil furnace | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 1,2 | MPaG | 0 | 1,2 | MPaG | 0.3 | 0.35 |  |  |  | MPaG |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C772/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C772 |  |  | 3107-PZT-74506B/3107-S-JB-C772 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 13 | [12 empty] | Запись в БД произведена
2069 | 3107 | 3107 | 3107-PZIA-74506C | SAI1000-01R | 3107-PZIA-74506C |  | 3107-Z-7466, 3107-Z-7491, 3107-Z-7497 | 3107-PZT-74506C | Р на выходе печи теплоносителя | Outlet pressure of thermal oil furnace | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7401 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 1,2 | MPaG | 0 | 1,2 | MPaG | 0.3 | 0.35 |  |  |  | MPaG |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C773/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C773 |  |  | 3107-PZT-74506C/3107-S-JB-C773 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 4 | [12 empty] | Запись в БД произведена
2071 | 3107 | 3107 | 3107-TZIA-74511 | SAI1000-01R | 3107-TZIA-74511 |  | new 3107-Z-7491 | 3107-TZT-74511 | Т змеевика теплоносителя | Heat conduction oil coil temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C771/3000-S-MC-B01 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C771 |  |  | 3107-TZT-74511/3107-S-JB-C771 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 9 | [12 empty] | Запись в БД произведена
2073 | 3107 | 3107 | 3107-TZIA-74512 | SAI1000-01R | 3107-TZIA-74512 |  | new 3107-Z-7491 | 3107-TZT-74512 | Т змеевика теплоносителя | Heat conduction oil coil temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C772/3000-S-MC-B01 | PR06 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C772 |  |  | 3107-TZT-74512/3107-S-JB-C772 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 1 | [12 empty] | Запись в БД произведена
2075 | 3107 | 3107 | 3107-TZIA-74513 | SAI1000-01R | 3107-TZIA-74513 |  | new 3107-Z-7491 | 3107-TZT-74513 | Т змеевика теплоносителя | Heat conduction oil coil temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | -50 | 400 | ℃ | -50 | 400 | ℃ |  |  | 285 | 288 |  | ℃ |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C773/3000-S-MC-B01 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 481 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C773 |  |  | 3107-TZT-74513/3107-S-JB-C773 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 7 | [12 empty] | Запись в БД произведена
2077 | 3107 | 3107 | 3107-PZIA-74503 | SAI1000-01R | 3107-PZIA-74503 |  | new 3107-Z-7491 | 3107-PZT-74503 | Р холодного воздуха на выходе вентилятора | Blower outlet cold air pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 12 | kPaG | 0 | 12 | kPaG | 0.2 | 0.3 |  |  |  | kPaG |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C771/3000-S-MC-B01 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C771 |  |  | 3107-PZT-74503/3107-S-JB-C771 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 5 | [12 empty] | Запись в БД произведена
2079 | 3107 | 3107 | 3107-PZIA-74504 | SAI1000-01R | 3107-PZIA-74504 |  | new 3107-Z-7491 | 3107-PZT-74504 | Р холодного воздуха на выходе вентилятора | Blower outlet cold air pressure | Pressure Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | 0 | 12 | kPaG | 0 | 12 | kPaG | 0.2 | 0.3 |  |  |  | kPaG |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C772/3000-S-MC-B01 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 481 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C772 |  |  | 3107-PZT-74504/3107-S-JB-C772 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 12 | [12 empty] | Запись в БД произведена
2081 | 3107 | 3107 | 3107-AZIA-74502 | SAI1000-01R | 3107-AZIA-74502 |  | new 3107-Z-7492, 3107-Z-7497 | 3107-AZT-74502 | Анализатор O2 в дымовых газах | Flue gas oxygen analyzer | O2 analyzer transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | AIR-EP | Exd | SIS | I | 230V AC 4-wire external Power | 0,48 | 0 | 25 | % | 0 | 25 | % | 0.5 | 2 |  |  |  | % |  |  | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-AZT-74502/3000-S-MC-B04 |  | NH-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B04 | Одиночный |  | 3107-AZT-74502/3000-S-MC-B04 | 3000-S-SC-B03 | 3000-S-MC-B04 |  | A31 | A32 | 06 | - | A31-06 | - | A32-06 | - | 1 | [12 empty] | Запись в БД произведена
2083 | 3107 | 3107 | 3107-BZA-74501 |  |  |  | new 3107-Z-7491, 3107-Z-7494 | 3107-BZE-74501 | Сигнал пламени | Flame signal | Ultraviolet flame detector | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B775/3000-S-MC-B11-01 |  | NH-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B11 | Одиночный |  | 3107-S-JB-B775/3000-S-MC-B11-01 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 18 | [12 empty] | Запись в БД произведена
2084 | 3107 | 3107 | 3107-BZA-74502 |  |  |  | new 3107-Z-7491, 3107-Z-7494 | 3107-BZE-74502 | Сигнал пламени | Flame signal | Ultraviolet flame detector | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B775/3000-S-MC-B11-02 |  | NH-DJYYP3 1x2x1.5 | 481 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B11 | Одиночный |  | 3107-S-JB-B775/3000-S-MC-B11-02 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 19 | [12 empty] | Запись в БД произведена
2086 | 3107 | 3107 | 3107-XZV-74501 | SKLPD0021-00 | 3107-XZV-74501 |  |  | 3107-XZV-74501 | Отс. клап. магистрали ПГ A | NG main On-off valve A | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 |  |  |  | SIS | [17 empty] | 3107-PK-7401 | ИД 2026 07 03
2087 | 3107 | 3107 | 3107-XZV-74501 | SKLPD0021-00 | 3107-XZV-74501 |  | new 3107-Z-7492, 3107-Z-7491, 3107-Z-7493, 3107-Z-7496, 3107-Z-7497, 3107-Z-6499 | 3107-XZY-74501 | Отс. клап. магистрали ПГ A | NG main On-off valve A | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B774/3000-S-MC-B13-02 | PR01 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B774 |  |  | 3107-XZY-74501/3107-S-JB-B774 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 24 | [12 empty] | Запись в БД произведена
2088 | 3107 | 3107 | 3107-XZV-74501 | SKLPD0021-00 | 3107-XZV-74501 |  |  | 3107-XZZSO-74501 | Отс. клап. магистрали ПГ A (открыт) | NG main On-off valve A | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR01 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSO-74501/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 3 | [12 empty] | Запись в БД произведена
2089 | 3107 | 3107 | 3107-XZV-74501 | SKLPD0021-00 | 3107-XZV-74501 |  |  | 3107-XZZSC-74501 | Отс. клап. магистрали ПГ A (закрыт) | NG main On-off valve A | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSC-74501/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 29 | [12 empty] | Запись в БД произведена
2091 | 3107 | 3107 | 3107-XZV-74502 | SKLPD0021-00 | 3107-XZV-74502 |  |  | 3107-XZV-74502 | Отс. клап. магистрали ПГ B | NG main On-off valve B | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 |  |  |  | SIS | [17 empty] | 3107-PK-7401 | ИД 2026 07 03
2092 | 3107 | 3107 | 3107-XZV-74502 | SKLPD0021-00 | 3107-XZV-74502 |  | new 3107-Z-7492, 3107-Z-7491, 3107-Z-7493, Z-7497, 3107-Z-7497 | 3107-XZY-74502 | Отс. клап. магистрали ПГ B | NG main On-off valve B | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B774/3000-S-MC-B13-02 | PR02 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B774 |  |  | 3107-XZY-74502/3107-S-JB-B774 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 25 | [12 empty] | Запись в БД произведена
2093 | 3107 | 3107 | 3107-XZV-74502 | SKLPD0021-00 | 3107-XZV-74502 |  |  | 3107-XZZSO-74502 | Отс. клап. магистрали ПГ B (открыт) | NG main On-off valve B | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSO-74502/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 4 | [12 empty] | Запись в БД произведена
2094 | 3107 | 3107 | 3107-XZV-74502 | SKLPD0021-00 | 3107-XZV-74502 |  |  | 3107-XZZSC-74502 | Отс. клап. магистрали ПГ B (закрыт) | NG main On-off valve B | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSC-74502/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 30 | [12 empty] | Запись в БД произведена
2096 | 3107 | 3107 | 3107-XZV-74503 | SKLPD0021-00 | 3107-XZV-74503 |  |  | 3107-XZV-74503 | Клапан сброса магистрали ПГ | NG main vent valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 |  |  |  | SIS | [17 empty] | 3107-PK-7401 | ИД 2026 07 03
2097 | 3107 | 3107 | 3107-XZV-74503 | SKLPD0021-00 | 3107-XZV-74503 |  | new 3107-Z-7492, 3107-Z-7491, 3107-Z-7493, Z-7497, 3107-Z-7497, 3107-Z-7496 | 3107-XZY-74503 | Клапан сброса магистрали ПГ | NG main vent valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B774/3000-S-MC-B13-02 | PR03 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B774 |  |  | 3107-XZY-74503/3107-S-JB-B774 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 26 | [12 empty] | Запись в БД произведена
2098 | 3107 | 3107 | 3107-XZV-74503 | SKLPD0021-00 | 3107-XZV-74503 |  |  | 3107-XZZSO-74503 | Клапан сброса магистрали ПГ (открыт) | NG main vent valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR05 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSO-74503/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 5 | [12 empty] | Запись в БД произведена
2099 | 3107 | 3107 | 3107-XZV-74503 | SKLPD0021-00 | 3107-XZV-74503 |  |  | 3107-XZZSC-74503 | Клапан сброса магистрали ПГ (закрыт) | NG main vent valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR06 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSC-74503/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 31 | [12 empty] | Запись в БД произведена
2101 | 3107 | 3107 | 3107-XZV-74504 | SKLPD0021-00 | 3107-XZV-74504 |  |  | 3107-XZV-74504 | Отс. клап. линии зажигания ПГ A | NG Ignition path On-off valve A | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 |  |  |  | SIS | [17 empty] | 3107-PK-7401 | ИД 2026 07 03
2102 | 3107 | 3107 | 3107-XZV-74504 | SKLPD0021-00 | 3107-XZV-74504 |  | new 3107-Z-7492, 3107-Z-7491, 3107-Z-7493, 3107-Z-7494, 3107-Z-7497, 3107-Z-6499 | 3107-XZY-74504 | Отс. клап. линии зажигания ПГ A | NG Ignition path On-off valve A | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B774/3000-S-MC-B13-02 | PR04 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B774 |  |  | 3107-XZY-74504/3107-S-JB-B774 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 27 | [12 empty] | Запись в БД произведена
2103 | 3107 | 3107 | 3107-XZV-74504 | SKLPD0021-00 | 3107-XZV-74504 |  |  | 3107-XZZSO-74504 | Отс. клап. линии зажигания ПГ A (открыт) | NG Ignition path On-off valve A | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR07 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSO-74504/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 6 | [12 empty] | Запись в БД произведена
2104 | 3107 | 3107 | 3107-XZV-74504 | SKLPD0021-00 | 3107-XZV-74504 |  |  | 3107-XZZSC-74504 | Отс. клап. линии зажигания ПГ A (закрыт) | NG Ignition path On-off valve A | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSC-74504/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 0 | [12 empty] | Запись в БД произведена
2106 | 3107 | 3107 | 3107-XZV-74505 | SKLPD0021-00 | 3107-XZV-74505 |  |  | 3107-XZV-74505 | Отс. клап. линии зажигания ПГ B | NG Ignition path On-off valve B | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 |  |  |  | SIS | [17 empty] | 3107-PK-7401 | ИД 2026 07 03
2107 | 3107 | 3107 | 3107-XZV-74505 | SKLPD0021-00 | 3107-XZV-74505 |  | new 3107-Z-7492, 3107-Z-7491, 3107-Z-7493, 3107-Z-7494, 3107-Z-7497 | 3107-XZY-74505 | Отс. клап. линии зажигания ПГ B | NG Ignition path On-off valve B | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B774/3000-S-MC-B13-02 | PR05 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B774 |  |  | 3107-XZY-74505/3107-S-JB-B774 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 28 | [12 empty] | Запись в БД произведена
2108 | 3107 | 3107 | 3107-XZV-74505 | SKLPD0021-00 | 3107-XZV-74505 |  |  | 3107-XZZSO-74505 | Отс. клап. линии зажигания ПГ B (открыт) | NG Ignition path On-off valve B | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSO-74505/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 7 | [12 empty] | Запись в БД произведена
2109 | 3107 | 3107 | 3107-XZV-74505 | SKLPD0021-00 | 3107-XZV-74505 |  |  | 3107-XZZSC-74505 | Отс. клап. линии зажигания ПГ B (закрыт) | NG Ignition path On-off valve B | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR10 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSC-74505/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 1 | [12 empty] | Запись в БД произведена
2111 | 3107 | 3107 | 3107-XZV-74506 | SKLPD0021-00 | 3107-XZV-74506 |  |  | 3107-XZV-74506 | Клапан сброса линии зажигания ПГ | NG Ignition path vent valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 |  |  |  | SIS | [17 empty] | 3107-PK-7401 | ИД 2026 07 03
2112 | 3107 | 3107 | 3107-XZV-74506 | SKLPD0021-00 | 3107-XZV-74506 |  | new 3107-Z-7492, 3107-Z-7491, 3107-Z-7493, 3107-Z-7494, 3107-Z-7497 | 3107-XZY-74506 | Клапан сброса линии зажигания ПГ | NG Ignition path vent valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B774/3000-S-MC-B13-02 | PR06 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B774 |  |  | 3107-XZY-74506/3107-S-JB-B774 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 02 | 03 | A33-02 | A33-03 | A34-02 | A34-03 | 29 | [12 empty] | Запись в БД произведена
2113 | 3107 | 3107 | 3107-XZV-74506 | SKLPD0021-00 | 3107-XZV-74506 |  |  | 3107-XZZSO-74506 | Клапан сброса линии зажигания ПГ (открыт) | NG Ignition path vent valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSO-74506/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 8 | [12 empty] | Запись в БД произведена
2114 | 3107 | 3107 | 3107-XZV-74506 | SKLPD0021-00 | 3107-XZV-74506 |  |  | 3107-XZZSC-74506 | Клапан сброса линии зажигания ПГ (закрыт) | NG Ignition path vent valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [14 empty] | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-C777/3000-S-MC-B05 | PR12 | NH-IA-DJYP3YP3 16x2x1.0 | 481 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C777 |  |  | 3107-XZZSC-74506/3107-S-JB-C777 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 2 | [12 empty] | Запись в БД произведена
2116 | 3107 | 3107 | 3107-BZI-74501 | SDO0001-01 | 3107-BZI-74501 |  | #N/A | 3107-BZI-74501 | Сигнал работы трансформатора зажигания | Ignition transformer working signal | Ignition transformer | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | 4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-S-JB-B774/3000-S-MC-B13-02 | PR07 | NH-KYJYP3 2x2.5 | 481 | 2x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-B774 |  |  | 3107-S-JB-B776/3107-S-JB-B774 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 18 | [12 empty] | Запись в БД произведена
2118 | 3107 | 3107 | 3107-HZS-74501 | SDI0010-01R | 3107-HZS-74501 |  | #N/A | 3107-HZS-74501 | Переключатель Местное/Дистанционное (1 сигн.) | Local/remote knob（1 contact signal） | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F02/3000-S-MC-B10-02 | PR04 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F02 |  |  | 3107-HZS-74501/3107-I-LP-F02 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 22 | [12 empty] | Запись в БД произведена
2120 | 3107 | 3107 | 3107-HZS-74502 | SDI0010-01R | 3107-HZS-74502 |  | #N/A | 3107-HZS-74502 | Кнопка Пуск на МЩУ | LCP-Start button | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F02/3000-S-MC-B10-02 | PR05 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F02 |  |  | 3107-HZS-74502/3107-I-LP-F02 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 23 | [12 empty] | Запись в БД произведена
2122 | 3107 | 3107 | 3107-HZS-74503 | SDI0010-01R | 3107-HZS-74503 |  | 3107-Z-7491 | 3107-HZS-74503 | Кнопка Стоп на МЩУ | LCP-Stop button | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F02/3000-S-MC-B10-02 | PR06 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F02 |  |  | 3107-HZS-74503/3107-I-LP-F02 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 16 | [12 empty] | Запись в БД произведена
2124 | 3107 | 3107 | 3107-HZS-74504 | SDI0010-01R | 3107-HZS-74504 |  | #N/A | 3107-HZS-74504 | Кнопка Сброс на МЩУ | LCP-Reset button | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F02/3000-S-MC-B10-02 | PR07 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F02 |  |  | 3107-HZS-74504/3107-I-LP-F02 | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 17 | [12 empty] | Запись в БД произведена
2126 | 3107 | 3107 | 3107-HZS-74505_1 | SDI0010-01R | 3107-HZS-74505-1 |  | 3107-Z-7492 | 3107-HZS-74505-1 | Кнопка Авар. останова на МЩУ-1 | LCP-Emergency button-1 | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 11 | [12 empty] | Запись в БД произведена
2128 | 3107 | 3107 | 3107-HZS-74505_2 | SDI0010-01R | 3107-HZS-74505-2 |  | 3107-Z-7492 | 3107-HZS-74505-2 | Кнопка Авар. останова на МЩУ-2 | LCP-Emergency button-2 | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 12 | [12 empty] | Запись в БД произведена
2130 | 3107 | 3107 | 3107-HZS-74505_3 | SDI0010-01R | 3107-HZS-74505-3 |  | 3107-Z-7492 | 3107-HZS-74505-3 | Кнопка Авар. останова на МЩУ-3 | LCP-Emergency button-3 | Button: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | 0 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 13 | [12 empty] | Запись в БД произведена
2132 | 3107 | 3107 | 3107-XZV-74501 | SKLPD0021-00 | 3107-XZV-74501 |  | #N/A | 3107-XZL-74501 | Лампа Готовность к розжигу на МЩУ | LCP-Ignition ready indicator light | Indicator light: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F02/3000-S-MC-B10-02 | PR01 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F02 |  |  | 3107-XZL-74501/3107-I-LP-F02 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 22 | [12 empty] | Запись в БД произведена
2134 | 3107 | 3107 | 3107-XZV-74502 | SKLPD0021-00 | 3107-XZV-74502 |  | #N/A | 3107-XZL-74502 | Лампа Работа на МЩУ | LCP-Running light | Indicator light: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F02/3000-S-MC-B10-02 | PR02 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F02 |  |  | 3107-XZL-74502/3107-I-LP-F02 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 23 | [12 empty] | Запись в БД произведена
2136 | 3107 | 3107 | 3107-XZV-74503 | SKLPD0021-00 | 3107-XZV-74503 |  | #N/A | 3107-XZL-74503 | Лампа Авария на МЩУ | LCP-Alarm light | Indicator light: LCP | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | LCP | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | 0,48 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 |  |  |  | 3107-I-LP-F02/3000-S-MC-B10-02 | PR03 | NH-DJYP3YP3 12x2x1.0 | 483 | 12x2x1.0mm2,NIS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-I-LP-F02 |  |  | 3107-XZL-74503/3107-I-LP-F02 | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 21 | [12 empty] | Запись в БД произведена
2138 | 2202 | 3107 | 3107-MXI-74520B | SDO0001-01 | 3107-MXI-74520B |  | #N/A | 3107-MXI-74520B | SIS пуск вентилятора воздуха горения 3107-BL-7402 | Combustion air blower 3107-BL-7402 SIS Start Command | SIS Start Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7421 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type/Loop No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 3 | [12 empty] | Запись в БД произведена
2140 | 2202 | 3107 | 3107-MXI-74520A | SDO0001-01 | 3107-MXI-74520A |  | 3107-Z-7492, 3107-Z-7491, 3107-Z-7493, 3107-Z-7494, 3107-Z-7497, 3107-Z-7496 | 3107-MXI-74520A | SIS стоп вентилятора воздуха горения 3107-BL-7402 | Combustion air blower 3107-BL-7402 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7421 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type/Loop No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 2 | [12 empty] | Запись в БД произведена
2142 | 2202 | 3107 | 3107-MXA-74520B | SDI0010-01R | 3107-MXA-74520B |  |  | 3107-MXA-74520B | Вентилятор воздуха горения 3107-BL-7402 работает | Combustion air blower 3107-BL-7402 Running | Running | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7421 | MCC | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type/Loop No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S06 |  | A70 | A71 | 14 | - | A70-14 | - | A71-14 | - | 1 | [12 empty] | Запись в БД произведена
2144 | 3107 | 3107 | 3107-YZS-74501 | SDO0001-01 | 3107-YZS-74501 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-74501 | 3107-B-7401 Состояние зажигания 1, SIS->DCS | 3107-B-7401 Ignition state 1, SIS to DCS， 3107-B-7401 Состояние зажигания 1, от SIS до DCS | When the furnace is in non-"operating mode”, the blower frequency MV and the main gas valve MV lock the ignition opening； In the "operating mode", the blower frequency MV and the main gas valve MV are unlocked. | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 28 | [12 empty] | Запись в БД произведена
2146 | 3107 | 3107 | 3107-YZS-74502 | SDO0001-01 | 3107-YZS-74502 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-74502 | 3107-B-7401 Состояние зажигания 2, SIS->DCS | 3107-B-7401 Ignition state 2, SIS to DCS， 3107-B-7401 Состояние зажигания 2, от SIS до DCS | The inverter of the blower is set to 0HZ | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 29 | [12 empty] | Запись в БД произведена
2148 | 3107 | 3107 | 3107-YZS-74503 | SDO0001-01 | 3107-YZS-74503 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-74503 | 3107-B-7401 Состояние зажигания 3, SIS->DCS | 3107-B-7401 Ignition state 3, SIS to DCS， 3107-B-7401 Состояние зажигания 3, от SIS до DCS | Air purge stage (Air purge before ignition stage + Air purge after stop stage) Blower frequency setting, purge opening | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 30 | [12 empty] | Запись в БД произведена
2150 | 3107 | 3107 | 3107-YZS-74504 | SDO0001-01 | 3107-YZS-74504 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-74504 | 3107-B-7401, SIS->DCS, закрыть отс. клап. Выхлопа | 3107-B-7401 , SIS to DCS，Close the exhaust gas on-off valve 3107-B-7401 ,Подключите SIS к DCS, закройте клапан включения-выключения выхлопных газов. | Close the exhaust gas on-off valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 31 | [12 empty] | Запись в БД произведена
2152 | 3107 | 3107 | 3107-YZS-74505 | SDO0001-01 | 3107-YZS-74505 |  | нет ИД по блокировкам ПАЗ->РСУ | 3107-YZS-74505 | 3107-B-7401, SIS->DCS, резерв | 3107-B-7401 , SIS to DCS，Spare 3107-B-7401 ,Подключите SIS к DCS, запасной |  | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-7421 | DCS | DOR-P | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [12 empty] | REV 4 | Update Loop No. & Tag No. | 3107-PK-7401 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 16 | [12 empty] | Запись в БД произведена
2154 | 3107 | 3107 | 3630-AZIA-66001 | SAI1000-01R | 3630-AZIA-66001 |  | 3630-Z-6602 | 3630-AZT-66001 | Содержание O2 в магистрали отх. газа | Tail Gas Mainpipe Oxygen Content | Laser gas analyzer | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | AIR-EP | Exp | SIS | I | 230V AC 4-wire external Power | SEE Power Supply List | 0 | 4 | vol% | 0 | 4 | vol% |  |  | 2 | 3 | 4 | vol% | REV 2 | Change instrument type | 3630-ACU-605 | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B04 |  | A31 | A32 | 06 | - | A31-06 | - | A32-06 | - | 4 | [12 empty] | Запись в БД произведена
2156 | 3109 | 3109 | 3630-FZIA-66006 | SAI1000-01R | 3630-FZIA-66006 |  | 3630-Z-6601 | 3630-FZT-66006 | Топливный газ к факелу для продувки | Fuel gas to purge flare header | Integral Orifice Flow Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 40 | kPa | 0 | 60 | kg/h | 25 | 30 |  |  |  | kg/h |  |  |  | ИД 2026 07 03 |  |  |  | 3109-S-JB-C437/3000-S-MC-B03 | PR10 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C437 |  |  | 3630-FZT-66006/3109-S-JB-C437 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 04 | - | A31-04 | - | A32-04 | - | 15 | [12 empty] | Запись в БД произведена
2158 | 3107 | 3107 | 3630-PZIA-66003A | SAI1000-01R | 3630-PZIA-66003A |  | 3630-Z-6602 | 3630-PZT-66003A | Р выхлопа в 3107-HF-6401 | Exhaust to 3107-HF-6401 pressure | Pressure transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -10 | 50 | kPaG | -10 | 50 | kPaG | 10 | 15 | 25 | 30 |  | kPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3630-PZT-66003A/3000-S-MC-B01 |  | NH-IA-DJYYP3 1x2x1.5 | 463 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B01 | Одиночный |  | 3630-PZT-66003A/3000-S-MC-B01 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 15 | [12 empty] | Запись в БД произведена
2159 | 3107 | 3107 | 3630-PZIA-66003B | SAI1000-01R | 3630-PZIA-66003B |  | 3630-Z-6602 | 3630-PZT-66003B | Р выхлопа в 3107-HF-6401 | Exhaust to 3107-HF-6401 pressure | Pressure transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -10 | 50 | kPaG | -10 | 50 | kPaG | 10 | 15 | 25 | 30 |  | kPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3630-PZT-66003B/3000-S-MC-B01 |  | NH-IA-DJYYP3 1x2x1.5 | 463 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B01 | Одиночный |  | 3630-PZT-66003B/3000-S-MC-B01 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 01 | - | A31-01 | - | A32-01 | - | 15 | [12 empty] | Запись в БД произведена
2160 | 3107 | 3107 | 3630-PZIA-66003C | SAI1000-01R | 3630-PZIA-66003C |  | 3630-Z-6602 | 3630-PZT-66003C | Р выхлопа в 3107-HF-6401 | Exhaust to 3107-HF-6401 pressure | Pressure transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -10 | 50 | kPaG | -10 | 50 | kPaG | 10 | 15 | 25 | 30 |  | kPaG |  |  |  | ИД 2026 07 03 |  |  |  | 3630-PZT-66003C/3000-S-MC-B01 |  | NH-IA-DJYYP3 1x2x1.5 | 463 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B01 | Одиночный |  | 3630-PZT-66003C/3000-S-MC-B01 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 02 | - | A31-02 | - | A32-02 | - | 15 | [12 empty] | Запись в БД произведена
2162 | 3109 | 3107 | 3630-XZV-66001 | SKLPD0021-00 | 3630-XZV-66001 |  |  | 3630-XZV-66001 | Отсечка отх. газа в атмосферу | Tail Gas to Vent cut-off | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
2163 | 3109 | 3107 | 3630-XZV-66001 | SKLPD0021-00 | 3630-XZV-66001 |  | 3630-Z-6602 | 3630-XZY-66001 | Отсечка отх. газа в атмосферу | Tail Gas to Vent cut-off | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D445/3000-S-MC-B13 | PR06 | NH-KYJYP3 24x2.5 | 335 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D445 |  |  | 3630-XZY-66001/3109-S-JB-D445 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 24 | [12 empty] | Запись в БД произведена
2164 | 3109 | 3107 | 3630-XZV-66001 | SKLPD0021-00 | 3630-XZV-66001 |  |  | 3630-XZZSC-66001 | Отсечка отх. газа в атмосферу (закрыт) | Tail Gas to Vent cut-off | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR13 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3630-XZZSC-66001/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 19 | [12 empty] | Запись в БД произведена
2165 | 3109 | 3107 | 3630-XZV-66001 | SKLPD0021-00 | 3630-XZV-66001 |  |  | 3630-XZZSO-66001 | Отсечка отх. газа в атмосферу (открыт) | Tail Gas to Vent cut-off | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR14 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3630-XZZSO-66001/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 21 | [12 empty] | Запись в БД произведена
2167 | 3109 | 3107 | 3630-XZV-66003 | SKLPD0021-00 | 3630-XZV-66003 |  |  | 3630-XZV-66003 | Отс. клап. N2 в 3107-HF-6401 | N2 flow to 3107-HF-6401 cut-off valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
2168 | 3109 | 3107 | 3630-XZV-66003 | SKLPD0021-00 | 3630-XZV-66003 |  | 3630-Z-6602 | 3630-XZY-66003 | Отс. клап. N2 в 3107-HF-6401 | N2 flow to 3107-HF-6401 cut-off valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D445/3000-S-MC-B13 | PR07 | NH-KYJYP3 24x2.5 | 335 | 24x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D445 |  |  | 3630-XZY-66003/3109-S-JB-D445 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 25 | [12 empty] | Запись в БД произведена
2169 | 3109 | 3107 | 3630-XZV-66003 | SKLPD0021-00 | 3630-XZV-66003 |  |  | 3630-XZZSC-66003 | Отс. клап. N2 в 3107-HF-6401 (закрыт) | N2 flow to 3107-HF-6401 cut-off valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR09 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3630-XZZSC-66003/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 20 | [12 empty] | Запись в БД произведена
2170 | 3109 | 3107 | 3630-XZV-66003 | SKLPD0021-00 | 3630-XZV-66003 |  |  | 3630-XZZSO-66003 | Отс. клап. N2 в 3107-HF-6401 (открыт) | N2 flow to 3107-HF-6401 cut-off valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C440/3000-S-MC-B08 | PR11 | NH-IA-DJYP3YP3 16x2x1.0 | 327 | 16x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C440 |  |  | 3630-XZZSO-66003/3109-S-JB-C440 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 22 | [12 empty] | Запись в БД произведена
2172 | 3107 | 3107 | 3630-XZV-66004 | SKLPD0021-00 | 3630-XZV-66004 |  |  | 3630-XZV-66004 | Отс. клап. выхлопа в 3107-HF-6401 | Exhaust to 3107-HF-6401 cut-off valve | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
2173 | 3107 | 3107 | 3630-XZV-66004 | SKLPD0021-00 | 3630-XZV-66004 |  | 3630-Z-6602 | 3630-XZY-66004 | Отс. клап. выхлопа в 3107-HF-6401 | Exhaust to 3107-HF-6401 cut-off valve | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-D407/3000-S-MC-B13 | PR02 | NH-KYJYP3 16x2.5 | 447 | 16x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3107-S-JB-D407 |  |  | 3630-XZY-66004/3107-S-JB-D407 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 5 | [12 empty] | Запись в БД произведена
2174 | 3107 | 3107 | 3630-XZV-66004 | SKLPD0021-00 | 3630-XZV-66004 |  |  | 3630-XZZSC-66004 | Отс. клап. выхлопа в 3107-HF-6401 (закрыт) | Exhaust to 3107-HF-6401 cut-off valve | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C404/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 447 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C404 |  |  | 3630-XZZSC-66004/3107-S-JB-C404 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 7 | [12 empty] | Запись в БД произведена
2175 | 3107 | 3107 | 3630-XZV-66004 | SKLPD0021-00 | 3630-XZV-66004 |  |  | 3630-XZZSO-66004 | Отс. клап. выхлопа в 3107-HF-6401 (открыт) | Exhaust to 3107-HF-6401 cut-off valve | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3107-S-JB-C404/3000-S-MC-B05 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 447 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3107-S-JB-C404 |  |  | 3630-XZZSO-66004/3107-S-JB-C404 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 09 | - | A31-09 | - | A32-09 | - | 8 | [12 empty] | Запись в БД произведена
2177 | 3109 | 3109 | 3630-XZV-66008 | SKLPD0021-00 | 3630-XZV-66008 |  |  | 3630-XZV-66008 | Отсечка MN к факелу для продувки | cut off MN flow to purge flare header | On-Off Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field |  |  | SIS | [18 empty] | ИД 2026 07 03
2178 | 3109 | 3109 | 3630-XZV-66008 | SKLPD0021-00 | 3630-XZV-66008 |  | 3630-Z-6601 | 3630-XZY-66008 | Отсечка MN к факелу для продувки | cut off MN flow to purge flare header | Solenoid Valve | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DOR-P | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤4 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-D443/3000-S-MC-B13 | PR12 | NH-KYJYP3 37x2.5 | 335 | 37x2.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3109-S-JB-D443 |  |  | 3630-XZY-66008/3109-S-JB-D443 | 3000-S-SC-B03 | 3000-S-MC-B13 |  | A33 | A34 | 04 | 05 | A33-04 | A33-05 | A34-04 | A34-05 | 10 | [12 empty] | Запись в БД произведена
2179 | 3109 | 3109 | 3630-XZV-66008 | SKLPD0021-00 | 3630-XZV-66008 |  |  | 3630-XZZSC-66008 | Отсечка MN к факелу для продувки (закрыт) | cut off MN flow to purge flare header | Limit Switch - Close | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C441/3000-S-MC-B07 | PR07 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C441 |  |  | 3630-XZZSC-66008/3109-S-JB-C441 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 28 | [12 empty] | Запись в БД произведена
2180 | 3109 | 3109 | 3630-XZV-66008 | SKLPD0021-00 | 3630-XZV-66008 |  |  | 3630-XZZSO-66008 | Отсечка MN к факелу для продувки (открыт) | cut off MN flow to purge flare header | Limit Switch - Open | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6604 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3109-S-JB-C441/3000-S-MC-B07 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 335 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3109-S-JB-C441 |  |  | 3630-XZZSO-66008/3109-S-JB-C441 | 3000-S-SC-B03 | 3000-S-MC-B07 |  | A31 | A32 | 11 | - | A31-11 | - | A32-11 | - | 29 | [12 empty] | Запись в БД произведена
2182 | 2202 | 3107 | 3630-MXI-76601A | SDO0001-01 | 3630-MXI-76601A |  | 3107-Z-6490 | 3630-MXI-76601A | SIS стоп вентилятора отх. газа 3630-BL-6601A | Exhaust Gas Blower 3630-BL-6601A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR008-6604 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 29 | [12 empty] | Запись в БД произведена
2184 | 2202 | 3107 | 3630-MXI-86601A | SDO0001-01 | 3630-MXI-86601A |  | 3107-Z-6490 | 3630-MXI-86601A | SIS стоп вентилятора отх. газа 3630-BL-6601B | Exhaust Gas Blower 3630-BL-6601B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR008-6604 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 30 | [12 empty] | Запись в БД произведена
2186 | 3101 | 3101 | 3608-LZIA-66061 | SAI1000-01R | 3608-LZIA-66061 |  | 3608-Z-6608 | 3608-LZT-66061 | Уровень в 3608-V-6604 | 3608-V-6604 Liquid level indication | Radar Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6606 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤2 | 0 | 1750 | mm | 0 | 100 | % | 20 | 25,71429 | 82,86 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3101-S-JB-C103/3000-S-MC-B01 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C103 |  |  | 3608-LZT-66061/3101-S-JB-C103 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 3 | [12 empty] | Запись в БД произведена
2188 | 3101 | 3101 | 3608-LZSA-66006 | SDI0010-01R | 3608-LZSA-66006 |  | 3608-Z-6608 | 3608-LZS-66006 | Ур. на выходе 3608-P-6606 | 3608-P-6606 outlet liquid indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6606 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C104/3000-S-MC-B08 | PR09 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C104 |  |  | 3608-LZS-66006/3101-S-JB-C104 | 3000-S-SC-B03 | 3000-S-MC-B08 |  | A31 | A32 | 12 | - | A31-12 | - | A32-12 | - | 8 | [12 empty] | Запись в БД произведена
2190 | 3101 | 3101 | 3608-TZIA-66372 | SAI1000-01R | 3608-TZIA-66372 |  | 3608-Z-6608 | 3608-TZT-66372 | Т подшипника 3608-P-6606 | 3608-P-6606 Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6606 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 80 |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3101-S-JB-C103/3000-S-MC-B01 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 407 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C103 |  |  | 3608-TZT-66372/3101-S-JB-C103 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 00 | - | A31-00 | - | A32-00 | - | 4 | [12 empty] | Запись в БД произведена
2191 | 2202 | 3101 | 3608-MXI-06606A | SDO0001-01 | 3608-MXI-06606A |  | 3608-Z-6608 | 3608-MXI-06606A | SIS стоп насоса воды парового конденсата 3608-P-6606 | Steam Condensate Drum Water Pump 3608-P-6606 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR008-6606 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 25 | [12 empty] | Запись в БД произведена
2193 | 3109 | 3604 | 3604-PZIA-66007A | SAI1000-01R | 3604-PZIA-66007A |  | 3604-Z-6610 ->(3000-Z-6295) | 3604-PZT-66007A | Р в 3604-V-6601 | 3604-V-6601 pressure indicator | Pressure Transmitter | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR008-6608 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 0,8 | MPaG | 0 | 0,8 | MPaG | 0,36 | 0,37 |  |  |  | MPaG | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3604-PZT-66007A/3000-S-MC-B02 |  | NH-IA-DJYYP3 1x2x1.5 | 360 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B02 | Одиночный |  | 3604-PZT-66007A/3000-S-MC-B02 | 3000-S-SC-B03 | 3000-S-MC-B01 |  | A31 | A32 | 03 | - | A31-03 | - | A32-03 | - | 15 | [12 empty] | Запись в БД произведена
2194 | 3109 | 3604 | 3604-PZIA-66007B | SAI1000-01R | 3604-PZIA-66007B |  | 3604-Z-6610 ->(3000-Z-6295) | 3604-PZT-66007B | Р в 3604-V-6601 | 3604-V-6601 pressure indicator | Pressure Transmitter | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR008-6608 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 0,8 | MPaG | 0 | 0,8 | MPaG | 0,36 | 0,37 |  |  |  | MPaG | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3604-PZT-66007B/3000-S-MC-B02 |  | NH-IA-DJYYP3 1x2x1.5 | 360 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B02 | Одиночный |  | 3604-PZT-66007B/3000-S-MC-B02 | 3000-S-SC-B03 | 3000-S-MC-B04 |  | A31 | A32 | 06 | - | A31-06 | - | A32-06 | - | 10 | [12 empty] | Запись в БД произведена
2195 | 3109 | 3604 | 3604-PZIA-66007C | SAI1000-01R | 3604-PZIA-66007C |  | 3604-Z-6610 ->(3000-Z-6295) | 3604-PZT-66007C | Р в 3604-V-6601 | 3604-V-6601 pressure indicator | Pressure Transmitter | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR008-6608 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | 0 | 0,8 | MPaG | 0 | 0,8 | MPaG | 0,36 | 0,37 |  |  |  | MPaG | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3604-PZT-66007C/3000-S-MC-B02 |  | NH-IA-DJYYP3 1x2x1.5 | 360 | 1x2x1.5mm2,IS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B02 | Одиночный |  | 3604-PZT-66007C/3000-S-MC-B02 | 3000-S-SC-B03 | 3000-S-MC-B04 |  | A33 | A34 | 06 | - | A33-06 | - | A34-06 | - | 0 | [12 empty] | Запись в БД произведена
2197 | 3104 | 3104 | 3620-LZSA-66007 | SDI0010-01R | 3620-LZSA-66007 |  | 3620-Z-6609 | 3620-LZS-66007 | Ур. на входе 3620-P-6607 | 3620-P-6607 Inlet liquid level indication | Tuning Fork | 3000_S_SC_B02 | SCS2 | 2490157-3000-PR008-6611 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | NEW |  | ИД 2026 07 03 |  |  |  | 3104-S-JB-C250/3000-S-MC-B06 | PR04 | NH-IA-DJYP3YP3 8x2x1.0 | 425 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3104-S-JB-C250 |  |  | 3620-LZS-66007/3104-S-JB-C250 | 3000-S-SC-B02 | 3000-S-MC-B08 |  | A21 | A22 | 13 | - | A21-13 | - | A22-13 | - | 25 | [12 empty] | Запись в БД произведена
2199 | 2202 | 3104 | 3620-MXI-06607A | SDO0001-01 | 3620-MXI-06607A |  | 3620-Z-6609 | 3620-MXI-06607A | SIS стоп насоса-повысителя давления CFW 3620-P-6607 | CFW Pipeline Booster Pump 3620-P-6607 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR008-6611 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | Update Loop No. & Tag No. &service& Instrument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 4 | [12 empty] | Запись в БД произведена
2201 | 3108 | 3108 | 3624-LZIA-66131 | SAI1000-01R | 3624-LZIA-66131 |  | 3624-Z-6605 | 3624-LZT-66131 | Индикация водной фазы в 3624-V-6603 | 3624-V-6603 Water phase Interface indication | Radar interface Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6613 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤2 | 550 | 1450 | mm | 0 | 100 | % | 5,555556 | 16,66667 | 92,22222 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3108-S-JB-C429/3000-S-MC-B03 | PR05 | NH-IA-DJYP3YP3 8x2x1.0 | 459 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C429 |  |  | 3624-LZT-66131/3108-S-JB-C429 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 7 | [12 empty] | Запись в БД произведена
2203 | 3108 | 3108 | 3624-LZIA-66132 | SAI1000-01R | 3624-LZIA-66132 |  | 3624-Z-6606 | 3624-LZT-66132 | Ур. масляной фазы в 3624-V-6603 | 3624-V-6603 Oil phase level indication | Radar Level Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6613 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤2 | 0 | 1950 | mm | 0 | 100 | % | 25,64103 | 31,28205 | 70,76923 |  |  | % |  |  |  | ИД 2026 07 03 |  |  |  | 3108-S-JB-C429/3000-S-MC-B03 | PR06 | NH-IA-DJYP3YP3 8x2x1.0 | 459 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C429 |  |  | 3624-LZT-66132/3108-S-JB-C429 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 8 | [12 empty] | Запись в БД произведена
2205 | 3108 | 3108 | 3624-LZSA-66002 | SDI0010-01R | 3624-LZSA-66002 |  | 3624-Z-6606 | 3624-LZS-66002 | Ур. на выходе 3624-P-6602 | 3624-P-6602 outlet liquid indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6613 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C426/3000-S-MC-B05 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 459 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C426 |  |  | 3624-LZS-66002/3108-S-JB-C426 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 10 | [12 empty] | Запись в БД произведена
2207 | 3108 | 3108 | 3624-LZSA-66005 | SDI0010-01R | 3624-LZSA-66005 |  | 3624-Z-6605 | 3624-LZS-66005 | Ур. на выходе 3624-P-6605 | 3624-P-6605 outlet liquid indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6613 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3108-S-JB-C426/3000-S-MC-B05 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 459 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C426 |  |  | 3624-LZS-66005/3108-S-JB-C426 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 10 | - | A31-10 | - | A32-10 | - | 11 | [12 empty] | Запись в БД произведена
2209 | 3108 | 3108 | 3624-TZIA-66370 | SAI1000-01R | 3624-TZIA-66370 |  | 3624-Z-6606 | 3624-TZT-66370 | Т подшипника 3624-P-6602 | 3624-P-6602 Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6613 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 80 |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3108-S-JB-C429/3000-S-MC-B03 | PR02 | NH-IA-DJYP3YP3 8x2x1.0 | 459 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C429 |  |  | 3624-TZT-66370/3108-S-JB-C429 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 9 | [12 empty] | Запись в БД произведена
2210 | 2202 | 3108 | 3624-MXI-06602A | SDO0001-01 | 3624-MXI-06602A |  | 3624-Z-6606, 3108-Z-6190 | 3624-MXI-06602A | SIS стоп масляного насоса закрытого дренажа 3624-P-6602 | Closed Drain Drum Oil Pump 3624-P-6602 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR008-6613 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 27 | [12 empty] | Запись в БД произведена
2212 | 3108 | 3108 | 3624-TZIA-66371 | SAI1000-01R | 3624-TZIA-66371 |  | 3624-Z-6605 | 3624-TZT-66371 | Т подшипника 3624-P-6605 | 3624-P-6605 Bearing temperature | Temperature Transmitter | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6613 | Field | AIR(I)-LP | Exi | SIS | B | 24V DC 2-wire Loop Power | ≤1 | -60 | 200 | ℃ | -60 | 200 | ℃ |  |  | 80 |  |  | ℃ |  |  |  | ИД 2026 07 03 |  |  |  | 3108-S-JB-C429/3000-S-MC-B03 | PR03 | NH-IA-DJYP3YP3 8x2x1.0 | 459 | 8x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3108-S-JB-C429 |  |  | 3624-TZT-66371/3108-S-JB-C429 | 3000-S-SC-B03 | 3000-S-MC-B03 |  | A31 | A32 | 05 | - | A31-05 | - | A32-05 | - | 10 | [12 empty] | Запись в БД произведена
2213 | 2202 | 3108 | 3624-MXI-06605A | SDO0001-01 | 3624-MXI-06605A |  | 3624-Z-6605, 3108-Z-6190 | 3624-MXI-06605A | SIS стоп водяного насоса закрытого дренажа 3624-P-6605 | Closed Drain Drum Water Pump 3624-P-6605 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR008-6613 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 28 | [12 empty] | Запись в БД произведена
2215 | 3101 | 3101 | 3624-LZSA-66001 | SDI0010-01R | 3624-LZSA-66001 |  | 3624-Z-6607 | 3624-LZS-66001 | Ур. на входе 3624-P-6601 | 3624-P-6601 Inlet liquid indication | Tuning Fork | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR008-6614 | Field | DIR(I)-NAMUR | Exi | SIS | B | 24V DC 2-wire Loop Power | 0,48 | [15 empty] | ИД 2026 07 03 |  |  |  | 3101-S-JB-C105/3000-S-MC-B05 | PR08 | NH-IA-DJYP3YP3 12x2x1.0 | 383 | 12x2x1.0mm2,IS,PE-INS/OS-PE-LSZH,Fire Resistant | 3101-S-JB-C105 |  |  | 3624-LZS-66001/3101-S-JB-C105 | 3000-S-SC-B03 | 3000-S-MC-B05 |  | A31 | A32 | 07 | - | A31-07 | - | A32-07 | - | 7 | [12 empty] | Запись в БД произведена
2217 | 2202 | 3109 | 3624-MXI-06601A | SDO0001-01 | 3624-MXI-06601A |  | 3101-Z-6008, Z-6607, 3624-Z-6607, 3109-Z-6707 | 3624-MXI-06601A | SIS стоп насоса КО сепаратора резинового р-ра 3624-P-6601 | Rubber Solution KO Drum Pump 3624-P-6601 SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR008-6614 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 2/REV 4 | Update Ex.type to Non-Ex/Update Instument type |  | ИД 2026 07 03 | [12 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A70 | A71 | 12 | 13 | A70-12 | A70-13 | A71-12 | A71-13 | 26 | [12 empty] | Запись в БД произведена
2219 | TITLE-005 | 3101 | 3101-HZS-60003A | SDI0010-01R | 3101-HZS-60003A |  | 3101-Z-6003 | 3101-HZS-60003A | Закрыть противопожарный клапан V-6001A | Close the rubber dissolving vessel 3101-V-6001A fire partition valve | Button: AUX | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 20 | [12 empty] | Запись в БД произведена
2220 | 3101 | 3101 | 3101-HZS-60003B | SDI0010-01R | 3101-HZS-60003B |  | 3101-Z-6003 | 3101-HZS-60003B | Закрыть противопожарный клапан V-6001A | Close the rubber dissolving vessel 3101-V-6001A fire partition valve | Local Button | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6002 | Field | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 |  |  |  | 3101-HZS-60003B/3000-S-MC-B11 |  | NH-DJYYP3 1x2x1.5 | 410 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B11 | Одиночный |  | 3101-HZS-60003B/3000-S-MC-B11 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 21 | [12 empty] | Запись в БД произведена
2222 | TITLE-005 | 3101 | 3101-HZS-60006A | SDI0010-01R | 3101-HZS-60006A |  | 3101-Z-6006 | 3101-HZS-60006A | Закрыть противопожарный клапан V-6001B | Close the rubber dissolving vessel 3101-V-6001B fire partition valve | Button: AUX | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 22 | [12 empty] | Запись в БД произведена
2223 | 3101 | 3101 | 3101-HZS-60006B | SDI0010-01R | 3101-HZS-60006B |  | 3101-Z-6006 | 3101-HZS-60006B | Закрыть противопожарный клапан V-6001B | Close the rubber dissolving vessel 3101-V-6001B fire partition valve | Local Button | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6003 | Field | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 |  |  |  | 3101-HZS-60006B/3000-S-MC-B11 |  | NH-DJYYP3 1x2x1.5 | 410 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B11 | Одиночный |  | 3101-HZS-60006B/3000-S-MC-B11 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 23 | [12 empty] | Запись в БД произведена
2225 | TITLE-005 | 3101 | 3101-HZS-60010A | SDI0010-01R | 3101-HZS-60010A |  | 3101-Z-6010 | 3101-HZS-60010A | Закрыть противопожарный клапан V-6002 | Close the RS Vessel 3101-V-6002 fire partition valve | Button: AUX | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 24 | [12 empty] | Запись в БД произведена
2226 | 3101 | 3101 | 3101-HZS-60010B | SDI0010-01R | 3101-HZS-60010B |  | 3101-Z-6010 | 3101-HZS-60010B | Закрыть противопожарный клапан V-6002 | Close the RS Vessel 3101-V-6002 fire partition valve | Local Button | 3000_S_SC_B03 | SCS3 | 2490157-3000-PR007-6004 | Field | DIR-VFC | Exd | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 |  |  |  | 3101-HZS-60010B/3000-S-MC-B11 |  | NH-DJYYP3 1x2x1.5 | 410 | 1x2x1.5mm2,NIS,PE-OS-PE-LSZH,Fire Resistant | 3000-S-MC-B11 | Одиночный |  | 3101-HZS-60010B/3000-S-MC-B11 | 3000-S-SC-B03 | 3000-S-MC-B11 |  | A31 | A32 | 14 | - | A31-14 | - | A32-14 | - | 25 | [12 empty] | Запись в БД произведена
2228 | TITLE-005 | 3000 | 3000-HZS-62000 | SDI0010-01R | 3000-HZS-62000 |  | 3000-Z-6295 | 3000-HZS-62000 | Останов установки ESD-2 | Process unit shut-down ESD-2 | Button: AUX | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6201 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [15 empty] | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 0 | [12 empty] | Запись в БД произведена
2229 | TITLE-005 |  | 3101-HZS-60090B | SDI0010-01R | 3101-HZS-60090B |  | 3101-Z-6090 | 3101-HZS-60090B | ESD-1 зона 3101 (вращ. оборуд.) | ESD-1 for area 3101 (rotating equipment) | Button: AUX | 3000_S_SC_B03 | SCS3 (SCS1->SCS3) | 2490157-3000-PR007-6001 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [15 empty] | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 1 | [12 empty] | Запись в БД произведена
2230 | TITLE-005 | Сombined Title | 3108-HZS-61090B | SDI0010-01R | 3108-HZS-61090B |  | 3108-Z-6190 | 3108-HZS-61090B | ESD-1 зона 3108 (вращ. оборуд.) | ESD-1 for area 3108 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (NEW) | 2490157-3000-PR007-6101 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 10 | [12 empty] | Запись в БД произведена
2231 | TITLE-005 | Сombined Title | 3102-HZS-62090B | SDI0010-01R | 3102-HZS-62090B |  | 3102-Z-6290 | 3102-HZS-62090B | ESD-1 зона 3102 (вращ. оборуд.) | ESD-1 for area 3102 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (NEW) | 2490157-3000-PR007-6201 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 0 | [12 empty] | Запись в БД произведена
2232 | TITLE-005 | Сombined Title | 3102-HZS-62090D | SDI0010-01R | 3102-HZS-62090D |  | 3102-Z-6290 | 3102-HZS-62090D | ESD-1 зона 3102 (вращ. оборуд.) | ESD-1 for area 3102 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (NEW) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 11 | [12 empty] | Запись в БД произведена
2233 | TITLE-005 | Сombined Title | 3102-HZS-62090F | SDI0010-01R | 3102-HZS-62090F |  | 3102-Z-6290 | 3102-HZS-62090F | ESD-1 зона 3102 (вращ. оборуд.) | ESD-1 for area 3102 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (NEW) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 12 | [12 empty] | Запись в БД произведена
2234 | TITLE-005 | Сombined Title | 3103-HZS-62092B | SDI0010-01R | 3103-HZS-62092B |  | 3103-Z-6292 | 3103-HZS-62092B | ESD-1 зона 3103 (вращ. оборуд.) | ESD-1 for area 3103 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (NEW) | 2490157-3000-PR007-6201 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 13 | [12 empty] | Запись в БД произведена
2235 | TITLE-005 | Сombined Title | 3106-HZS-63090B | SDI0010-01R | 3106-HZS-63090B |  | 3106-Z-6390 | 3106-HZS-63090B | ESD-1 зона 3106 (вращ. оборуд.) | ESD-1 for area 3106 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (NEW) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 14 | [12 empty] | Запись в БД произведена
2236 | TITLE-005 | Сombined Title | 3110-HZS-63092B | SDI0010-01R | 3110-HZS-63092B |  | 3110-Z-6392 | 3110-HZS-63092B | ESD-1 зона 3110 (вращ. оборуд.) | ESD-1 for area 3110 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (NEW) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 15 | [12 empty] | Запись в БД произведена
2237 | TITLE-005 | Сombined Title | 3107-HZS-64090B | SDI0010-01R | 3107-HZS-64090B |  | 3107-Z-6490 | 3107-HZS-64090B | ESD-1 зона 3107 (вращ. оборуд.) | ESD-1 for area 3107 (rotating equipment) | Button: AUX | 3000_S_SC_B03 | SCS3 (NEW) | 2490157-3000-PR007-6401 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 2 | [12 empty] | Запись в БД произведена
2238 | TITLE-005 |  | 3107-HZS-64090F | SDI0010-01R | 3107-HZS-64090F |  | 3107-Z-6490 | 3107-HZS-64090F | ESD-1 зона 3107 (вращ. оборуд.) | ESD-1 for area 3107 (rotating equipment) | Button: AUX | 3000_S_SC_B03 | SCS3 (NEW) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 14 | [12 empty] | Запись в БД произведена
2239 | TITLE-005 | 3109 | 3109-HZS-67090B | SDI0010-01R | 3109-HZS-67090B |  | 3109-Z-6790 | 3109-HZS-67090B | ESD-1 зона 3109 (вращ. оборуд.) | ESD-1 for area 3109 (rotating equipment) | Button: AUX | 3000_S_SC_B03 | SCS3 (NEW) | 2490157-3000-PR007-6701 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 3 | [12 empty] | Запись в БД произведена
2240 | TITLE-005 | 3109 | 3109-HZS-67090F | SDI0010-01R | 3109-HZS-67090F |  | 3109-Z-6790 | 3109-HZS-67090F | ESD-1 зона 3109 (вращ. оборуд.) | ESD-1 for area 3109 (rotating equipment) | Button: AUX | 3000_S_SC_B03 | SCS3 (NEW) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 15 | [12 empty] | Запись в БД произведена
2241 | TITLE-005 | Сombined Title | 3104-HZS-72090B | SDI0010-01R | 3104-HZS-72090B |  | 3104-Z-7290 | 3104-HZS-72090B | ESD-1 зона 3104 (вращ. оборуд.) | ESD-1 for area 3104 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 | 2490157-3000-PR007-7201 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 1 | [12 empty] | Запись в БД произведена
2242 | TITLE-005 | Сombined Title | 3104-HZS-72090D | SDI0010-01R | 3104-HZS-72090D |  | 3104-Z-7290 | 3104-HZS-72090D | ESD-1 зона 3104 (вращ. оборуд.) | ESD-1 for area 3104 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (New) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 16 | [12 empty] | Запись в БД произведена
2243 | TITLE-005 | Сombined Title | 3104-HZS-72090F | SDI0010-01R | 3104-HZS-72090F |  | 3104-Z-7290 | 3104-HZS-72090F | ESD-1 зона 3104 (вращ. оборуд.) | ESD-1 for area 3104 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (New) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 17 | [12 empty] | Запись в БД произведена
2244 | TITLE-005 | Сombined Title | 3105-HZS-72092B | SDI0010-01R | 3105-HZS-72092B |  | 3105-Z-7292 | 3105-HZS-72092B | ESD-1 зона 3105 (вращ. оборуд.) | ESD-1 for area 3105 (rotating equipment) | Button: AUX | 3000_S_SC_B01 | SCS1 (New) | 2490157-3000-PR007-7201 | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 18 | [12 empty] | Запись в БД произведена
2245 | TITLE-005 |  |  |  | SPARE |  |  | SPARE | Резервная кнопка | Spare Botton | Button: AUX | 3000_S_SC_B01 | SCS1 (NEW) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 19 | [12 empty] | Запись в БД произведена
2246 | TITLE-005 |  | 3000-MOS-10001 | SDI0010-01R | 3000-MOS-10001 |  |  | 3000-MOS-10001 | PS MOS Включен | PS MOS Enabled | Switch: AUX | 3000_S_SC_B01 | SCS1 (NEW) |  | AUX | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | Update Tag No. | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 20 | [12 empty] | Запись в БД произведена
2247 | TITLE-005 |  | 3000-MOS-10002 | SDO0001-01 | 3000-MOS-10002 |  |  | 3000-MOS-10002 | PS MOS Включен | PS MOS Enabled | Light（Yellow） | 3000_S_SC_B01 | SCS1 (NEW) |  | AUX | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 27 | [12 empty] | Запись в БД произведена
2248 | TITLE-005 |  | 3000-MOS-10003 | SDO0001-01 | 3000-MOS-10003 |  |  | 3000-MOS-10003 | PS MOS Таймаут | PS MOS Timeout | Light（Red） | 3000_S_SC_B01 | SCS1 (NEW) |  | AUX | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 28 | [12 empty] | Запись в БД произведена
2250 | 2201 |  | 3010-GZY-10001 | SDI0010-01R | 3010-GZY-10001 |  | Из GDS для: 3101-Z-6090, 3101-Z-6091 | 3010-GZY-10001 | SIS от GDS, сигналы межсист. 3101-Z-6090, 3101-Z-6091 | SIS from GDS, inter-system communication signals 3101-Z-6090, 3101-Z-6091 | Relay | 3000_S_SC_B03 | SCS3 (NEW) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 4 | [12 empty] | Запись в БД произведена
2251 | 2201 | 3110 | 3010-GZY-10002 | SDI0010-01R | 3010-GZY-10002 |  | из GDS для: 3108-Z-6190, 3108-Z-6191 | 3010-GZY-10002 | SIS от GDS, сигналы межсист. 3108-Z-6190, 3108-Z-6191 | SIS from GDS, inter-system communication signals 3108-Z-6190, 3108-Z-6191 | Relay | 3000_S_SC_B01 | SCS1 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 2 | [12 empty] | Запись в БД произведена
2252 | 2201 | 3110 | 3010-GZY-10003 | SDI0010-01R | 3010-GZY-10003 |  | из GDS для: 3102-Z-6290, 3102-Z-6291 | 3010-GZY-10003 | SIS от GDS, сигналы межсист. 102-Z-6290, 3102-Z-6091 | SIS from GDS, inter-system communication signals 102-Z-6290, 3102-Z-6091 | Relay | 3000_S_SC_B01 | SCS1 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 3 | [12 empty] | Запись в БД произведена
2253 | 2201 | 3110 | 3010-GZY-10004 | SDI0010-01R | 3010-GZY-10004 |  | Из GDS для: 3103-Z-6292, 3103-Z-6293 | 3010-GZY-10004 | SIS от GDS, сигналы межсист. связи | SIS from GDS, inter-system communication signals | Relay | 3000_S_SC_B01 | SCS1 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 4 | [12 empty] | Запись в БД произведена
2254 | 2201 | 3110 | 3010-GZY-10005 | SDI0010-01R | 3010-GZY-10005 |  | Из GDS для: 3106-Z-6390, 3106-Z-6391 | 3010-GZY-10005 | SIS от GDS, сигналы межсист. связи | SIS from GDS, inter-system communication signals | Relay | 3000_S_SC_B01 | SCS1 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 5 | [12 empty] | Запись в БД произведена
2255 | 2201 | 3110 | 3010-GZY-10006 | SDI0010-01R | 3010-GZY-10006 |  | Из GDS для: 3107-Z-6402 | 3010-GZY-10006 | SIS от GDS, сигналы межсист. связи | SIS from GDS, inter-system communication signals | Relay | 3000_S_SC_B03 | SCS3 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 5 | [12 empty] | Запись в БД произведена
2256 | 2201 | 3110 | 3010-GZY-10007 | SDI0010-01R | 3010-GZY-10007 |  | Из GDS для:3107-Z-6490, 3107-Z-6499 | 3010-GZY-10007 | SIS от GDS, сигналы межсист. связи | SIS from GDS, inter-system communication signals | Relay | 3000_S_SC_B03 | SCS3 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 6 | [12 empty] | Запись в БД произведена
2257 | 2201 | 3110 | 3010-GZY-10008 | SDI0010-01R | 3010-GZY-10008 |  | Из GDS для: 3109-Z-6790, 3109-Z-6791 | 3010-GZY-10008 | SIS от GDS, сигналы межсист. связи | SIS from GDS, inter-system communication signals | Relay | 3000_S_SC_B03 | SCS3 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B03 | 3000-S-MC-B10 |  | A31 | A32 | 15 | - | A31-15 | - | A32-15 | - | 7 | [12 empty] | Запись в БД произведена
2258 | 2201 | 3110 | 3010-GZY-10009 | SDI0010-01R | 3010-GZY-10009 |  | Из GDS для: 3104-Z-7290, 3104-Z-7291 | 3010-GZY-10009 | SIS от GDS, сигналы межсист. связи | SIS from GDS, inter-system communication signals | Relay | 3000_S_SC_B01 | SCS1 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 6 | [12 empty] | Запись в БД произведена
2259 | 2201 | 3110 | 3010-GZY-10010 | SDI0010-01R | 3010-GZY-10010 |  | Из GDS для: 3105-Z-7292, 3105-Z-7293 | 3010-GZY-10010 | SIS от GDS, сигналы межсист. связи | SIS from GDS, inter-system communication signals | Relay | 3000_S_SC_B01 | SCS1 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 7 | [12 empty] | Запись в БД произведена
2260 | 2201 | 3110 | 3010-GZY-10011 | SDI0010-01R | 3010-GZY-10011 |  | Из GDS для: Резерв | 3010-GZY-10011 | SIS от GDS, сигналы межсист. (резерв) | SIS from GDS, inter-system communication signals(spare) | Relay | 3000_S_SC_B01 | SCS1 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 8 | [12 empty] | Запись в БД произведена
2261 | 2201 | 3110 | 3010-GZY-10012 | SDI0010-01R | 3010-GZY-10012 |  | Из GDS для: Резерв | 3010-GZY-10012 | SIS от GDS, сигналы межсист. (резерв) | SIS from GDS, inter-system communication signals(spare) | Relay | 3000_S_SC_B01 | SCS1 (переехал из SCS2) |  | GDS | DIR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 3 | new |  | ИД 2026 07 03 | [12 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 9 | [12 empty] | Запись в БД произведена
2263 | 3103 | [6 empty] | 3103-P-6231A | SIS стоп вакуумной системы финальной дегазации A 3103-P-6231A | Final Devolatilizer Vacuum System A 3103-P-6231A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6221 | Field | [18 empty] | REV 4 | NEW
2264 | 2202 |  | 3103-MXI-06231A | SDO0001-01 | 3103-MXI-06231A |  | 3103-Z-6292 | 3103-MXI-06231A | SIS стоп вакуумной системы финальной дегазации A 3103-P-6231A | Final Devolatilizer Vacuum System A 3103-P-6231A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6221 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 5 | [12 empty] | Запись в БД произведена
2266 | 3103 | [6 empty] | 3103-P-6232A | SIS стоп роторного двигателя 1 вак. системы A 3103-P-6232A | Final Devolatilizer Vacuum System A Roots motors 1 3103-P-6232A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6221 | Field | [18 empty] | REV 4 | NEW
2267 | 2202 |  | 3103-MXI-06232A | SDO0001-01 | 3103-MXI-06232A |  | 3103-Z-6292 | 3103-MXI-06232A | SIS стоп роторного двигателя 1 вак. системы A 3103-P-6232A | Final Devolatilizer Vacuum System A Roots motors 1 3103-P-6232A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6221 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 6 | [12 empty] | Запись в БД произведена
2269 | 3103 | [6 empty] | 3103-P-6233A | SIS стоп роторного двигателя 2 вак. системы A 3103-P-6233A | Final Devolatilizer Vacuum System A Roots motors 2 3103-P-6233A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6221 | Field | [18 empty] | REV 4 | NEW
2270 | 2202 |  | 3103-MXI-06233A | SDO0001-01 | 3103-MXI-06233A |  | 3103-Z-6292 | 3103-MXI-06233A | SIS стоп роторного двигателя 2 вак. системы A 3103-P-6233A | Final Devolatilizer Vacuum System A Roots motors 2 3103-P-6233A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6221 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 7 | [12 empty] | Запись в БД произведена
2272 | 3103 | [6 empty] | 3103-P-6231B | SIS стоп вакуумной системы финальной дегазации B 3103-P-6231B | Final Devolatilizer Vacuum System B 3103-P-6231B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6222 | Field | [18 empty] | REV 4 | NEW
2273 | 2202 |  | 3103-MXI-16231A | SDO0001-01 | 3103-MXI-16231A |  | 3103-Z-6292 | 3103-MXI-16231A | SIS стоп вакуумной системы финальной дегазации B 3103-P-6231B | Final Devolatilizer Vacuum System B 3103-P-6231B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6222 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 8 | [12 empty] | Запись в БД произведена
2275 | 3103 | [6 empty] | 3103-P-6232B | SIS стоп роторного двигателя 1 вак. системы B 3103-P-6232B | Final Devolatilizer Vacuum System B Roots motors 1 3103-P-6232B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6222 | Field | [18 empty] | REV 4 | NEW
2276 | 2202 |  | 3103-MXI-16232A | SDO0001-01 | 3103-MXI-16232A |  | 3103-Z-6292 | 3103-MXI-16232A | SIS стоп роторного двигателя 1 вак. системы B 3103-P-6232B | Final Devolatilizer Vacuum System B Roots motors 1 3103-P-6232B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6222 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 9 | [12 empty] | Запись в БД произведена
2278 | 3103 | [6 empty] | 3103-P-6233B | SIS стоп роторного двигателя 2 вак. системы B 3103-P-6233B | Final Devolatilizer Vacuum System B Roots motors 2 3103-P-6233B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6222 | Field | [18 empty] | REV 4 | NEW
2279 | 2202 |  | 3103-MXI-16233A | SDO0001-01 | 3103-MXI-16233A |  | 3103-Z-6292 | 3103-MXI-16233A | SIS стоп роторного двигателя 2 вак. системы B 3103-P-6233B | Final Devolatilizer Vacuum System B Roots motors 2 3103-P-6233B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6222 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 10 | [12 empty] | Запись в БД произведена
2281 | 3103 | [6 empty] | 3103-P-6214A | SIS стоп вторичной вакуумной системы A 3103-P-6214A | Secondary Vacuum System A 3103-P-6214A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6223 | Field | [18 empty] | REV 4 | NEW
2282 | 2202 |  | 3103-MXI-06214A | SDO0001-01 | 3103-MXI-06214A |  | 3103-Z-6292 | 3103-MXI-06214A | SIS стоп вторичной вакуумной системы A 3103-P-6214A | Secondary Vacuum System A 3103-P-6214A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6223 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 11 | [12 empty] | Запись в БД произведена
2284 | 3103 | [6 empty] | 3103-P-6214B | SIS стоп вторичной вакуумной системы B 3103-P-6214B | Secondary Vacuum System B 3103-P-6214B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6223 | Field | [18 empty] | REV 4 | NEW
2285 | 2202 |  | 3103-MXI-16214A | SDO0001-01 | 3103-MXI-16214A |  | 3103-Z-6292 | 3103-MXI-16214A | SIS стоп вторичной вакуумной системы B 3103-P-6214B | Secondary Vacuum System B 3103-P-6214B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-6223 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 12 | [12 empty] | Запись в БД произведена
2287 | 3102 | [6 empty] | 3103-P-6215A | SIS стоп вакуумной системы полимеризатора A 3103-P-6215A | Polymerizer Vacuum System A 3103-P-6215A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6224 | Field | [18 empty] | REV 4 | NEW
2288 | 2202 |  | 3103-MXI-06215A | SDO0001-01 | 3103-MXI-06215A |  | 3102-Z-6290 | 3103-MXI-06215A | SIS стоп вакуумной системы полимеризатора A 3103-P-6215A | Polymerizer Vacuum System A 3103-P-6215A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC | 2490157-3000-PR007-6224 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 21 | [12 empty] | Запись в БД произведена
2290 | 3102 | [6 empty] | 3103-P-6215B | SIS стоп вакуумной системы полимеризатора B 3103-P-6215B | Polymerizer Vacuum System B 3103-P-6215B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-6224 | Field | [18 empty] | REV 4 | NEW
2291 | 2202 |  | 3103-MXI-16215A | SDO0001-01 | 3103-MXI-16215A |  | 3102-Z-6290 | 3103-MXI-16215A | SIS стоп вакуумной системы полимеризатора B 3103-P-6215B | Polymerizer Vacuum System B 3103-P-6215B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC | 2490157-3000-PR007-6224 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 22 | [12 empty] | Запись в БД произведена
2293 | 3105 | [6 empty] | 3105-P-7231A | SIS стоп вакуумной системы финальной дегазации A 3105-P-7231A | Final Devolatilizer Vacuum System A 3105-P-7231A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7221 | Field | [18 empty] | REV 4 | NEW
2294 | 2202 |  | 3105-MXI-07231A | SDO0001-01 | 3105-MXI-07231A |  | 3105-Z-7292 | 3105-MXI-07231A | SIS стоп вакуумной системы финальной дегазации A 3105-P-7231A | Final Devolatilizer Vacuum System A 3105-P-7231A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7221 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 13 | [12 empty] | Запись в БД произведена
2296 | 3105 | [6 empty] | 3105-P-7232A | SIS стоп роторного двигателя 1 вак. системы A 3105-P-7232A | Final Devolatilizer Vacuum System A Roots motors 1 3105-P-7232A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7221 | Field | [18 empty] | REV 4 | NEW
2297 | 2202 |  | 3105-MXI-07232A | SDO0001-01 | 3105-MXI-07232A |  | 3105-Z-7292 | 3105-MXI-07232A | SIS стоп роторного двигателя 1 вак. системы A 3105-P-7232A | Final Devolatilizer Vacuum System A Roots motors 1 3105-P-7232A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7221 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 14 | [12 empty] | Запись в БД произведена
2299 | 3105 | [6 empty] | 3105-P-7233A | SIS стоп роторного двигателя 2 вак. системы A 3105-P-7233A | Final Devolatilizer Vacuum System A Roots motors 2 3105-P-7233A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7221 | Field | [18 empty] | REV 4 | NEW
2300 | 2202 |  | 3105-MXI-07233A | SDO0001-01 | 3105-MXI-07233A |  | 3105-Z-7292 | 3105-MXI-07233A | SIS стоп роторного двигателя 2 вак. системы A 3105-P-7233A | Final Devolatilizer Vacuum System A Roots motors 2 3105-P-7233A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7221 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 15 | [12 empty] | Запись в БД произведена
2302 | 3105 | [6 empty] | 3105-P-7231B | SIS стоп вакуумной системы финальной дегазации B 3105-P-7231B | Final Devolatilizer Vacuum System B 3105-P-7231B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7222 | Field | [18 empty] | REV 4 | NEW
2303 | 2202 |  | 3105-MXI-17231A | SDO0001-01 | 3105-MXI-17231A |  | 3105-Z-7292 | 3105-MXI-17231A | SIS стоп вакуумной системы финальной дегазации B 3105-P-7231B | Final Devolatilizer Vacuum System B 3105-P-7231B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7222 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 16 | [12 empty] | Запись в БД произведена
2305 | 3105 | [6 empty] | 3105-P-7232B | SIS стоп роторного двигателя 1 вак. системы B 3105-P-7232B | Final Devolatilizer Vacuum System B Roots motors 1 3105-P-7232B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7222 | Field | [18 empty] | REV 4 | NEW
2306 | 2202 |  | 3105-MXI-17232A | SDO0001-01 | 3105-MXI-17232A |  | 3105-Z-7292 | 3105-MXI-17232A | SIS стоп роторного двигателя 1 вак. системы B 3105-P-7232B | Final Devolatilizer Vacuum System B Roots motors 1 3105-P-7232B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7222 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 17 | [12 empty] | Запись в БД произведена
2308 | 3105 | [6 empty] | 3105-P-7233B | SIS стоп роторного двигателя 2 вак. системы B 3105-P-7233B | Final Devolatilizer Vacuum System B Roots motors 2 3105-P-7233B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7222 | Field | [18 empty] | REV 4 | NEW
2309 | 2202 |  | 3105-MXI-17233A | SDO0001-01 | 3105-MXI-17233A |  | 3105-Z-7292 | 3105-MXI-17233A | SIS стоп роторного двигателя 2 вак. системы B 3105-P-7233B | Final Devolatilizer Vacuum System B Roots motors 2 3105-P-7233B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7222 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 18 | [12 empty] | Запись в БД произведена
2311 | 3105 | [6 empty] | 3105-P-7214A | SIS стоп вторичной вакуумной системы A 3105-P-7214A | Secondary Vacuum System A 3105-P-7214A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7223 | Field | [18 empty] | REV 4 | NEW
2312 | 2202 |  | 3105-MXI-07214A | SDO0001-01 | 3105-MXI-07214A |  | 3105-Z-7292 | 3105-MXI-07214A | SIS стоп вторичной вакуумной системы A 3105-P-7214A | Secondary Vacuum System A 3105-P-7214A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7223 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 19 | [12 empty] | Запись в БД произведена
2314 | 3105 | [6 empty] | 3105-P-7214B | SIS стоп вторичной вакуумной системы B 3105-P-7214B | Secondary Vacuum System B 3105-P-7214B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7223 | Field | [18 empty] | REV 4 | NEW
2315 | 2202 |  | 3105-MXI-17214A | SDO0001-01 | 3105-MXI-17214A |  | 3105-Z-7292 | 3105-MXI-17214A | SIS стоп вторичной вакуумной системы B 3105-P-7214B | Secondary Vacuum System B 3105-P-7214B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC(SCS1) | 2490157-3000-PR007-7223 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 20 | [12 empty] | Запись в БД произведена
2317 | 3104 | [6 empty] | 3105-P-7215A | SIS стоп вакуумной системы полимеризатора A 3105-P-7215A | Polymerizer Vacuum System A 3105-P-7215A SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7224 | Field | [18 empty] | REV 4 | NEW
2318 | 2202 |  | 3105-MXI-07215A | SDO0001-01 | 3105-MXI-07215A |  | 3104-Z-7290 | 3105-MXI-07215A | SIS стоп вакуумной системы полимеризатора A 3105-P-7215A | Polymerizer Vacuum System A 3105-P-7215A SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC | 2490157-3000-PR007-7224 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 23 | [12 empty] | Запись в БД произведена
2320 | 3104 | [6 empty] | 3105-P-7215B | SIS стоп вакуумной системы полимеризатора B 3105-P-7215B | Polymerizer Vacuum System B 3105-P-7215B SIS Stop Command | Motor |  |  | 2490157-3000-PR007-7224 | Field | [18 empty] | REV 4 | NEW
2321 | 2202 |  | 3105-MXI-17215A | SDO0001-01 | 3105-MXI-17215A |  | 3104-Z-7290 | 3105-MXI-17215A | SIS стоп вакуумной системы полимеризатора B 3105-P-7215B | Polymerizer Vacuum System B 3105-P-7215B SIS Stop Command | SIS Stop Command | 3000_S_SC_B01 | MCC | 2490157-3000-PR007-7224 | MCC | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire | ≤1 | [12 empty] | REV 4 | NEW | [14 empty] | 2202-S-RC-S03 | 2202-S-RC-S05 |  | A72 | A73 | 00 | 01 | A72-00 | A72-01 | A73-00 | A73-01 | 24 | [12 empty] | Запись в БД произведена
2323 | 2201 |  | 3010-DZY-20001 | SDO0001-01 | 3010-DZY-20001 |  | 3104-Z-7290, 3104-I-7290 | 3010-DZY-20001 | SIS->DCS, сигналы межсист. 3104-Z-7290, 3104-I-7290 | SIS to DCS, inter-system communication signals 3104-Z-7290, 3104-I-7290 | Relay | 3000_S_SC_B01 | SCS1 (New) |  | DCS | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | new | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 29 | [12 empty] | Запись в БД произведена
2324 | 2201 |  | 3010-DZY-20002 | SDO0001-01 | 3010-DZY-20002 |  | 3106-Z-6390 -> 3106-I-6390 | 3010-DZY-20002 | SIS->DCS, сигналы межсист. 3106-Z-6390->3106-I-6390 | SIS to DCS, inter-system communication signals 3106-Z-6390 -> 3106-I-6390 | Relay | 3000_S_SC_B01 | SCS1 (NEW) |  | DCS | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | new | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 30 | [12 empty] | Запись в БД произведена
2325 | 2201 |  | 3010-DZY-20003 | SDO0001-01 | 3010-DZY-20003 |  | 3110-Z-6392 -> 3110-I-6392 | 3010-DZY-20003 | SIS->DCS, сигналы межсист. Связи | SIS to DCS, inter-system communication signals | Relay | 3000_S_SC_B01 | SCS1 (NEW) |  | DCS | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | new | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B12 |  | A13 | A14 | 02 | 03 | A13-02 | A13-03 | A14-02 | A14-03 | 31 | [12 empty] | Запись в БД произведена
2326 | 2201 |  | 3010-DZY-20004 | SDO0001-01 | 3010-DZY-20004 |  | 3107-Z-6491, 3107-Z-6492, 3107-Z-6493, 3107-Z-6497, 3107-Z-6499. SCS3->FCS1 (3107) (3107-XV-64507) | 3010-DZY-20004 | SIS->DCS, сигналы межсист. 3107-Z-6491->Закрыть 3107-XY-64507 | SIS to DCS, inter-system communication signals 3107-Z-6491 -> Close 3107-XY-64507 | Relay | 3000_S_SC_B03 | SCS3 (NEW) |  | DCS | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | new | [14 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 26 | [12 empty] | Запись в БД произведена
2327 | 2201 |  | 3010-DZY-20005 | SDO0001-01 | 3010-DZY-20005 |  | 3107-Z-7492, 3107-Z-7491, 3107-Z-7493, 3107-Z-7497, 3107-Z-6499. SCS3->FCS1 (3107) (3107-XV-74507) | 3010-DZY-20005 | SIS->DCS, сигналы межсист. Связи | SIS to DCS, inter-system communication signals | Relay | 3000_S_SC_B03 | SCS3 (NEW) |  | DCS | DOR-VFC | Non-Ex | SIS | R | 24V DC 2-wire Loop Power | ≤1 | [12 empty] | REV 4 | new | [14 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 07 | 08 | A33-07 | A33-08 | A34-07 | A34-08 | 27 | [12 empty] | Запись в БД произведена
2329 | TITLE-005 |  | 3101-HZS-60001 | SDO0001-01 | 3101-HZS-60001 |  | 3101-Z-6014 | 3101-HZS-60001 | Блок. отсечных клапанов P-6001A/B | The on-off valves on the inlet and outlet pipes of RS delivery pump 3101-P-6001A/B interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6002 | SIS | S | [17 empty] | REV 4 | new
2330 | TITLE-005 |  | 3101-HZS-60002 | SDO0001-01 | 3101-HZS-60002 |  | 3101-Z-6017 | 3101-HZS-60002 | Блок. отсечных клапанов P-6002 и P-6003A/B | The on-off valve on on the inlet and outlet pipes of RS circulation pump 3101-P-6002 and RS feed pump 3101-P-6003A/B interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6004 | SIS | S | [17 empty] | REV 4 | new
2331 | TITLE-005 |  | 3101-HZS-60090A | SDO0001-01 | 3101-HZS-60090A |  | 3101-Z-6090 | 3101-HZS-60090A | ESD-1 зона 3101 (вращ. оборуд.) | ESD-1 for area 3101 (rotating equipment) | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6001 | SIS | S | [17 empty] | REV 4 | new
2332 | TITLE-005 |  | 3101-HZS-60091 | SDO0001-01 | 3101-HZS-60091 |  | 3101-Z-6091 | 3101-HZS-60091 | ESD-1 зона 3101 (отсечные клапаны) | ESD-1 for area 3101 (shut-off valve) | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6001 | SIS | S | [17 empty] | REV 4 | new
2333 | TITLE-005 |  | 3101-HZS-61001 | SDO0001-01 | 3101-HZS-61001 |  | 3101-Z-6106 | 3101-HZS-61001 | Блок. отсечных клапанов P-6101A/B/C/D | The on-off valve on the inlet and outlet pipes of Dye Feed pump 3101-P-6101A/B/C/D interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6102 | SIS | S | [17 empty] | REV 4 | new
2334 | TITLE-005 |  | 3101-HZS-61002 | SDO0001-01 | 3101-HZS-61002 |  | 3101-Z-6109 | 3101-HZS-61002 | Блок. отсечных клапанов P-6102A/B/C/D | The on-off valve on the inlet and outlet pipes of RA Feed pump 3101-P-6102A/B/C/D interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6103 | SIS | S | [17 empty] | REV 4 | new
2335 | TITLE-005 |  | 3101-HZS-61003 | SDO0001-01 | 3101-HZS-61003 |  | 3101-Z-6112 | 3101-HZS-61003 | Блок. отсечных клапанов P-6104A/B | The on-off valve on the inlet and outlet pipes of Initiator Feed pump 3101-P-6104A/B interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6105 | SIS | S | [17 empty] | REV 4 | new
2336 | TITLE-005 |  | 3101-HZS-61004 | SDO0001-01 | 3101-HZS-61004 |  | 3101-Z-6113 | 3101-HZS-61004 | Блок. отсечных клапанов P-6104C/D | The on-off valve on the inlet and outlet pipes of Initiator Feed pump 3101-P-6104C/D interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6105 | SIS | S | [17 empty] | REV 4 | new
2337 | TITLE-005 |  | 3101-HZS-61005 | SDO0001-01 | 3101-HZS-61005 |  | 3101-Z-6115 | 3101-HZS-61005 | Блок. отсечных клапанов P-6106A/B/C/D | The on-off valve on the inlet and outlet pipes of EB Feed pump 3101-P-6106A/B/C/D interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6106 | SIS | S | [17 empty] | REV 4 | new
2338 | TITLE-005 |  | 3101-HZS-61006 | SDO0001-01 | 3101-HZS-61006 |  | 3101-Z-6117 | 3101-HZS-61006 | Блок. отсечных клапанов P-6107A/B/C/D | The on-off valve on the inlet and outlet of MO Feed pump 3101-P-6107A/B/C/D interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6107 | SIS | S | [17 empty] | REV 4 | new
2339 | TITLE-005 |  | 3108-HZS-61007 | SDO0001-01 | 3108-HZS-61007 |  | 3108-Z-6119 | 3108-HZS-61007 | Блок. отсечных клапанов P-6105A/B | The on-off valve on the inlet and outlet of Mercaptan Feed pump 3108-P-6105A/B interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6108 | SIS | S | [17 empty] | REV 4 | new
2340 | TITLE-005 |  | 3101-HZS-61008 | SDO0001-01 | 3101-HZS-61008 |  | 3101-Z-6121 | 3101-HZS-61008 | Блок. отсечных клапанов P-6108A/B | The on-off valve on the inlet and outlet of Special MO Feed pump 3101-P-6108A/B interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6109 | SIS | S | [17 empty] | REV 4 | new
2341 | TITLE-005 |  | 3108-HZS-61090A | SDO0001-01 | 3108-HZS-61090A |  | 3108-Z-6190 | 3108-HZS-61090A | ESD-1 зона 3108 (вращ. оборуд.) | ESD-1 for area 3108 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6101 | SIS | S | [17 empty] | REV 4 | new
2342 | TITLE-005 |  | 3108-HZS-61091 | SDO0001-01 | 3108-HZS-61091 |  | 3108-Z-6191 | 3108-HZS-61091 | ESD-1 зона 3108 (отсечные клапаны) | ESD-1 for area 3108 (shut-off valve) | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6101 | SIS | S | [17 empty] | REV 4 | new
2343 | TITLE-005 |  | 3102-HZS-62001A | SDO0001-01 | 3102-HZS-62001A |  | 3102-Z-6201 | 3102-HZS-62001A | Блок. останова подогревателя сырья E-6201 | Feedstock Preheater 3102-E-6201 interlock shutdown | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6201 | SIS | S | [17 empty] | REV 4 | new
2344 | TITLE-005 |  | 3102-HZS-62002 | SDO0001-01 | 3102-HZS-62002 |  | 3102-Z-6202 | 3102-HZS-62002 | Блок. останова R-6201 при Т HH1 | The First Pre-Polymerizer 3102-R-6201 interlocks and stops due to HH1 temperature | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6202 | SIS | S | [17 empty] | REV 4 | new
2345 | TITLE-005 |  | 3102-HZS-62003 | SDO0001-01 | 3102-HZS-62003 |  | 3102-Z-6203 | 3102-HZS-62003 | Блок. останова R-6201 при Т HH2 | The First Pre-Polymerizer 3102-R-6201 interlocks and stops when the temperature HH2 | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6202 | SIS | S | [17 empty] | REV 4 | new
2346 | TITLE-005 |  | 3102-HZS-62024 | SDO0001-01 | 3102-HZS-62024 |  | 3102-Z-6203 | 3102-HZS-62024 | Блок. останова R-6201 при Т HH2 | The First Pre-Polymerizer 3102-R-6201 interlocks and stops when the temperature HH2 | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2347 | TITLE-005 |  | 3102-HZS-62004 | SDO0001-01 | 3102-HZS-62004 |  | 3102-Z-6204 | 3102-HZS-62004 | Блок. останова R-6201 при Р HH | The First Pre-Polymerizer 3102-R-6201 pressure HH interlock stop | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6202 | SIS | S | [17 empty] | REV 4 | new
2348 | TITLE-005 |  | 3102-HZS-62005A | SDO0001-01 | 3102-HZS-62005A |  | 3102-Z-6205 | 3102-HZS-62005A | Блок. останова P-6201A | The First Pre-Polymerizer Melt Pump 3102-P-6201A interlocks and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6203 | SIS | S | [17 empty] | REV 4 | new
2349 | TITLE-005 |  | 3102-HZS-62006A | SDO0001-01 | 3102-HZS-62006A |  | 3102-Z-6206 | 3102-HZS-62006A | Блок. останова P-6201B | The First Pre-Polymerizer Melt Pump 3102-P-6201B interlocks and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6203 | SIS | S | [17 empty] | REV 4 | new
2350 | TITLE-005 |  | 3102-HZS-62007 | SDO0001-01 | 3102-HZS-62007 |  | 3102-Z-6207 | 3102-HZS-62007 | Блок. останова R-6202 при Т HH1 | The Second Pre-Polymerizer 3102-R-6202 interlocks and stops due to HH1 temperature | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6204 | SIS | S | [17 empty] | REV 4 | new
2351 | TITLE-005 |  | 3102-HZS-62010 | SDO0001-01 | 3102-HZS-62010 |  | 3102-Z-6208 | 3102-HZS-62010 | Блок. останова R-6202 при Т HH2 | The Second Pre-Polymerizer 3102-R-6202 interlocks and stops when the temperature is HH2 | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6204 | SIS | S | [17 empty] | REV 4 | new
2352 | TITLE-005 |  | 3102-HZS-62025 | SDO0001-01 | 3102-HZS-62025 |  | 3102-Z-6208 | 3102-HZS-62025 | Блок. останова R-6202 при Т HH2 | The Second Pre-Polymerizer 3102-R-6202 interlocks and stops when the temperature is HH2 | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2353 | TITLE-005 |  | 3102-HZS-62009 | SDO0001-01 | 3102-HZS-62009 |  | 3102-Z-6209 | 3102-HZS-62009 | Блок. останова R-6202 при Р HH | The Second Pre-Polymerizer 3102-R-6202 has HH pressure interlocking and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6204 | SIS | S | [17 empty] | REV 4 | new
2354 | TITLE-005 |  | 3102-HZS-62010A | SDO0001-01 | 3102-HZS-62010A |  | 3102-Z-6210 | 3102-HZS-62010A | Блок. останова P-6203A | The Second Pre-Polymerizer Melt Pump 3102-P-6203A interlocks and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6205 | SIS | S | [17 empty] | REV 4 | new
2355 | TITLE-005 |  | 3102-HZS-62011A | SDO0001-01 | 3102-HZS-62011A |  | 3102-Z-6211 | 3102-HZS-62011A | Блок. останова P-6203B | The Second Pre-Polymerizer Melt Pump 3102-P-6203B interlocks and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6205 | SIS | S | [17 empty] | REV 4 | new
2356 | TITLE-005 |  | 3102-HZS-62012A | SDO0001-01 | 3102-HZS-62012A |  | 3102-Z-6212 | 3102-HZS-62012A | Блок. останова P-6205A | The First Polymerizer Melt Pump 3102-P-6205A interlocking stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6206 | SIS | S | [17 empty] | REV 4 | new
2357 | TITLE-005 |  | 3102-HZS-62013A | SDO0001-01 | 3102-HZS-62013A |  | 3102-Z-6213 | 3102-HZS-62013A | Блок. останова P-6205B | The First Polymerizer Melt Pump 3102-P-6205B interlocks and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6206 | SIS | S | [17 empty] | REV 4 | new
2358 | TITLE-005 |  | 3102-HZS-62014A | SDO0001-01 | 3102-HZS-62014A |  | 3102-Z-6214 | 3102-HZS-62014A | Блок. останова P-6206A | The Second Polymerizer Melt Pump 3102-P-6206A interlocks and stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6207 | SIS | S | [17 empty] | REV 4 | new
2359 | TITLE-005 |  | 3102-HZS-62015A | SDO0001-01 | 3102-HZS-62015A |  | 3102-Z-6215 | 3102-HZS-62015A | Блок. останова P-6206B | The Second Polymerizer Melt Pump 3102-P-6206B interlocks and stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6207 | SIS | S | [17 empty] | REV 4 | new
2360 | TITLE-005 |  | 3102-HZS-62016A | SDO0001-01 | 3102-HZS-62016A |  | 3102-Z-6216 | 3102-HZS-62016A | Блок. останова P-6207A | The Third Polymerizer Melt Pump 3102-P-6207A interlocking stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6208 | SIS | S | [17 empty] | REV 4 | new
2361 | TITLE-005 |  | 3102-HZS-62017A | SDO0001-01 | 3102-HZS-62017A |  | 3102-Z-6217 | 3102-HZS-62017A | Блок. останова P-6207B | The Third Polymerizer Melt Pump 3102-P-6207B interlocks and stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6208 | SIS | S | [17 empty] | REV 4 | new
2362 | TITLE-005 |  | 3103-HZS-62018A | SDO0001-01 | 3103-HZS-62018A |  | 3103-Z-6218 | 3103-HZS-62018A | Блок. останова P-6208A | Main devolatilizer melt pump 3103-P-6208A interlocking shutdown | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6209 | SIS | S | [17 empty] | REV 4 | new
2363 | TITLE-005 |  | 3103-HZS-62019A | SDO0001-01 | 3103-HZS-62019A |  | 3103-Z-6219 | 3103-HZS-62019A | Блок. останова P-6208B | Main devolatilizer melt pump 3103-P-6208B interlocking shutdown | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6209 | SIS | S | [17 empty] | REV 4 | new
2364 | TITLE-005 |  | 3103-HZS-62020A | SDO0001-01 | 3103-HZS-62020A |  | 3103-Z-6220 | 3103-HZS-62020A | Блок. останова P-6209A | Final devolatilizer melt pump 3103-P-6209A interlocking shutdown | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6210 | SIS | S | [17 empty] | REV 4 | new
2365 | TITLE-005 |  | 3103-HZS-62021A | SDO0001-01 | 3103-HZS-62021A |  | 3103-Z-6221 | 3103-HZS-62021A | Блок. останова P-6209B | Final devolatilizer melt pump 3103-P-6209B interlocking shutdown | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6210 | SIS | S | [17 empty] | REV 4 | new
2366 | TITLE-005 |  | 3102-HZS-62102 | SDO0001-01 | 3102-HZS-62102 |  | 3102-Z-6247 | 3102-HZS-62102 | Блок. отсечных клапанов P-6202A/B | The on-off valve on the inlet and outlet of First Pre-Polymerizer Reflux Pump 3102-P-6202A/B interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6202 | SIS | S | [17 empty] | REV 4 | new
2367 | TITLE-005 |  | 3102-HZS-62104 | SDO0001-01 | 3102-HZS-62104 |  | 3102-Z-6248 | 3102-HZS-62104 | Блок. отсечных клапанов P-6204A/B | The on-off valve on the inlet and outlet of Second Pre-Polymerizer Reflux Pump 3102-P-6204A/B | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6204 | SIS | S | [17 empty] | REV 4 | new
2368 | TITLE-005 |  | 3103-HZS-62110 | SDO0001-01 | 3103-HZS-62110 |  | 3103-Z-6240 | 3103-HZS-62110 | Блок. отсечных клапанов P-6210A/B | The on-off valve on the inlet and outlet of Final Devolatilizer Condensate Pump 3103-P-6210A/B interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6211 | SIS | S | [17 empty] | REV 4 | new
2369 | TITLE-005 |  | 3103-HZS-62011 | SDO0001-01 | 3103-HZS-62011 |  | 3103-Z-6241 | 3103-HZS-62011 | Блок. отсечных клапанов P-6211A/B | The on-off valve on the inlet and outlet of Purification Column Kettle Pump 3103-P-6211A/B interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6212 | SIS | S | [17 empty] | REV 4 | new
2370 | TITLE-005 |  | 3103-HZS-62012 | SDO0001-01 | 3103-HZS-62012 |  | 3103-Z-6242 | 3103-HZS-62012 | Блок. отсечных клапанов P-6212A/B | The on-off valve on the inlet and outlet of Purification Column Reflux Pump 3103-P-6212A/B interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6213 | SIS | S | [17 empty] | REV 4 | new
2371 | TITLE-005 |  | 3103-HZS-62022 | SDO0001-01 | 3103-HZS-62022 |  | 3103-Z-6243 | 3103-HZS-62022 | Блок. отсечных клапанов P-6218A/B | The on-off valve on the inlet and outlet of Devolatilization Vacuum Sealing Liquid Pump 3103-P-6218A/B interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6215 | SIS | S | [17 empty] | REV 4 | new
2372 | TITLE-005 |  | 3103-HZS-62023 | SDO0001-01 | 3103-HZS-62023 |  | 3103-Z-6244 | 3103-HZS-62023 | Блок. отсечных клапанов P-6219A/B | The on-off valve on the inlet and outlet of Pre-Polymerizer Vacuum Sealing Liquid Pump 3103-P-6219A/B interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6215 | SIS | S | [17 empty] | REV 4 | new
2373 | TITLE-005 |  | 3103-HZS-62016 | SDO0001-01 | 3103-HZS-62016 |  | 3103-Z-6245 | 3103-HZS-62016 | Блок. отсечных клапанов P-6216A/B | The on-off valve on the inlet and outlet of Oily Water Extraction Pump 3103-P-6216A/B interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6216 | SIS | S | [17 empty] | REV 4 | new
2374 | TITLE-005 |  | 3103-HZS-62017 | SDO0001-01 | 3103-HZS-62017 |  | 3103-Z-6246 | 3103-HZS-62017 | Блок. отсечных клапанов P-6217 | The on-off valve on the inlet and outlet of Separator Oil Pump 3103-P-6217 interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6216 | SIS | S | [17 empty] | REV 4 | new
2375 | TITLE-005 |  | 3102-HZS-62090A | SDO0001-01 | 3102-HZS-62090A |  | 3102-Z-6290 | 3102-HZS-62090A | ESD-1 зона 3102 (вращ. оборуд.) | ESD-1 for area 3102 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6201 | SIS | S | [17 empty] | REV 4 | new
2376 | TITLE-005 |  | 3102-HZS-62090C | SDO0001-01 | 3102-HZS-62090C |  | 3102-Z-6290 | 3102-HZS-62090C | ESD-1 зона 3102 (вращ. оборуд.) | ESD-1 for area 3102 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2377 | TITLE-005 |  | 3102-HZS-62090E | SDO0001-01 | 3102-HZS-62090E |  | 3102-Z-6290 | 3102-HZS-62090E | ESD-1 зона 3102 (вращ. оборуд.) | ESD-1 for area 3102 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2378 | TITLE-005 |  | 3102-HZS-62091 | SDO0001-01 | 3102-HZS-62091 |  | 3102-Z-6291 | 3102-HZS-62091 | ESD-1 зона 3102 (отсечные клапаны) | ESD-1 for area 3102 (shut-off valve) | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6201 | SIS | S | [17 empty] | REV 4 | new
2379 | TITLE-005 |  | 3103-HZS-62092A | SDO0001-01 | 3103-HZS-62092A |  | 3103-Z-6292 | 3103-HZS-62092A | ESD-1 зона 3103 (вращ. оборуд.) | ESD-1 for area 3103 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6201 | SIS | S | [17 empty] | REV 4 | new
2380 | TITLE-005 |  | 3103-HZS-62093 | SDO0001-01 | 3103-HZS-62093 |  | 3103-Z-6293 | 3103-HZS-62093 | ESD-1 зона 3103 (отсечные клапаны) | ESD-1 for area 3103 (shut-off valve) | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2381 | TITLE-005 |  | 3106-HZS-63090A | SDO0001-01 | 3106-HZS-63090A |  | 3106-Z-6390 | 3106-HZS-63090A | ESD-1 зона 3106 (вращ. оборуд.) | ESD-1 for area 3106 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2382 | TITLE-005 |  | 3110-HZS-63092A | SDO0001-01 | 3110-HZS-63092A |  | 3110-Z-6392 | 3110-HZS-63092A | ESD-1 зона 3110 (вращ. оборуд.) | ESD-1 for area 3110 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2383 | TITLE-005 |  | 3107-HZS-64002 | SDO0001-01 | 3107-HZS-64002 |  | 3107-Z-6402 | 3107-HZS-64002 | Блок. паровой завесы | Steam curtain interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6401 | SIS | S | [17 empty] | REV 4 | new
2384 | TITLE-005 |  | 3107-HZS-64019 | SDO0001-01 | 3107-HZS-64019 |  | 3107-Z-6451 | 3107-HZS-64019 | Блок. отсечных клапанов HOP-6401ABC | The on-off valve on the inlet and outlet of Hot HTF Circulation Pump 3107-HOP-6401ABC interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6409 | SIS | S | [17 empty] | REV 4 | new
2385 | TITLE-005 |  | 3107-HZS-64003 | SDO0001-01 | 3107-HZS-64003 |  | 3107-Z-6453 | 3107-HZS-64003 | Блок. отсечных клапанов HOP-6403ABC | The on-off valve on the inlet and outlet of Warm HTF Circulation Pump 3107-HOP-6403ABC interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6402 | SIS | S | [17 empty] | REV 4 | new
2386 | TITLE-005 |  | 3107-HZS-64004 | SDO0001-01 | 3107-HZS-64004 |  | 3107-Z-6454 | 3107-HZS-64004 | Блок. отсечных клапанов HOP-6404AB | The on-off valve on the inlet and outlet of Feedstock Preheater HTF Pump 3107-HOP-6404AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6402 | SIS | S | [17 empty] | REV 4 | new
2387 | TITLE-005 |  | 3107-HZS-64005 | SDO0001-01 | 3107-HZS-64005 |  | 3107-Z-6455 | 3107-HZS-64005 | Блок. отсечных клапанов HOP-6405AB | The on-off valve on the inlet and outlet of First Pre-Polymerizer HTF Pump 3107-HOP-6405AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6403 | SIS | S | [17 empty] | REV 4 | new
2388 | TITLE-005 |  | 3107-HZS-64006 | SDO0001-01 | 3107-HZS-64006 |  | 3107-Z-6456 | 3107-HZS-64006 | Блок. отсечных клапанов HOP-6406AB | The on-off valve on the inlet and outlet of Second Pre-Polymerizer HTF Pump 3107-HOP-6406AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6403 | SIS | S | [17 empty] | REV 4 | new
2389 | TITLE-005 |  | 3107-HZS-64007 | SDO0001-01 | 3107-HZS-64007 |  | 3107-Z-6457 | 3107-HZS-64007 | Блок. отсечных клапанов HOP-6407A/B | The on-off valve on the inlet and outlet of First Polymerizer HTF Pump 3107-P-6407A/B interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6404 | SIS | S | [17 empty] | REV 4 | new
2390 | TITLE-005 |  | 3107-HZS-64017 | SDO0001-01 | 3107-HZS-64017 |  | 3107-Z-6467 | 3107-HZS-64017 | Блок. отсечных клапанов HOP-6407BC | The on-off valve on the inlet and outlet of First Polymerizer HTF Pump 3107-HOP-6407BC interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6404 | SIS | S | [17 empty] | REV 4 | new
2391 | TITLE-005 |  | 3107-HZS-64008 | SDO0001-01 | 3107-HZS-64008 |  | 3107-Z-6458 | 3107-HZS-64008 | Блок. отсечных клапанов HOP-6408AB | The on-off valve on the inlet and outlet of Second Polymerizer HTF Pump 3107-HOP-6408AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6405 | SIS | S | [17 empty] | REV 4 | new
2392 | TITLE-005 |  | 3107-HZS-64018 | SDO0001-01 | 3107-HZS-64018 |  | 3107-Z-6468 | 3107-HZS-64018 | Блок. отсечных клапанов HOP-6408BC | The on-off valve on the inlet and outlet of Second Polymerizer HTF Pump 3107-HOP-6408BC interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6405 | SIS | S | [17 empty] | REV 4 | new
2393 | TITLE-005 |  | 3107-HZS-64009 | SDO0001-01 | 3107-HZS-64009 |  | 3107-Z-6459 | 3107-HZS-64009 | Блок. отсечных клапанов HOP-6409 | The on-off valve on the inlet and outlet of Third Polymerizer Upper HTF Pump 3107-HOP-6409 interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6406 | SIS | S | [17 empty] | REV 4 | new
2394 | TITLE-005 |  | 3107-HZS-64010 | SDO0001-01 | 3107-HZS-64010 |  | 3107-Z-6460 | 3107-HZS-64010 | Блок. отсечных клапанов HOP-6410AB | The on-off valve on the inlet and outlet of Third Polymerizer Lower HTF Pump 3107-HOP-6410AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6406 | SIS | S | [17 empty] | REV 4 | new
2395 | TITLE-005 |  | 3107-HZS-64011 | SDO0001-01 | 3107-HZS-64011 |  | 3107-Z-6461 | 3107-HZS-64011 | Блок. отсечных клапанов HOP-6411AB | The on-off valve on the inlet and outlet of Devolatilization Heater HTF Pump 3107-HOP-6411AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6407 | SIS | S | [17 empty] | REV 4 | new
2396 | TITLE-005 |  | 3107-HZS-64012 | SDO0001-01 | 3107-HZS-64012 |  | 3107-Z-6462 | 3107-HZS-64012 | Блок. отсечных клапанов HOP-6412AB | The on-off valve on the inlet and outlet of Main Devolatilization Sytem HTF Pump 3107-HOP-6412AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6408 | SIS | S | [17 empty] | REV 4 | new
2397 | TITLE-005 |  | 3107-HZS-64013 | SDO0001-01 | 3107-HZS-64013 |  | 3107-Z-6463 | 3107-HZS-64013 | Блок. отсечных клапанов HOP-6413AB | The on-off valve on the inlet and outlet of Final Devolatilization System HTF PUMP 3107-HOP-6413AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6408 | SIS | S | [17 empty] | REV 4 | new
2398 | TITLE-005 |  | 3107-HZS-64014 | SDO0001-01 | 3107-HZS-64014 |  | 3107-Z-6464 | 3107-HZS-64014 | Блок. отсечных клапанов HOP-6414A | The on-off valve on the inlet and outlet of Melt Heat Exchanger HTF Pump A 3107-HOP-6414A interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6411 | SIS | S | [17 empty] | REV 4 | new
2399 | TITLE-005 |  | 3107-HZS-64114 | SDO0001-01 | 3107-HZS-64114 |  | 3107-Z-6465 | 3107-HZS-64114 | Блок. отсечных клапанов HOP-6414B | The on-off valve on the inlet and outlet of Melt Heat Exchanger HTF Pump B 3107-HOP-6414B interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-6411 | SIS | S | [17 empty] | REV 4 | new
2400 | TITLE-005 |  | 3107-HZS-64100 | SDO0001-01 | 3107-HZS-64100 |  | 3107-Z-6470 | 3107-HZS-64100 | Блок. отсечных клапанов HOP-6001 | The on-off valve on the inlet and outlet of Dissolution Heater HTF Pump 3107-HOP-6001 interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6407 | SIS | S | [17 empty] | REV 4 | new
2401 | TITLE-005 |  | 3107-HZS-64090A | SDO0001-01 | 3107-HZS-64090A |  | 3107-Z-6490 | 3107-HZS-64090A | ESD-1 зона 3107 (вращ. оборуд.) | ESD-1 for area 3107 (rotating equipment) | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6401 | SIS | S | [17 empty] | REV 4 | new
2402 | TITLE-005 |  | 3107-HZS-64090E | SDO0001-01 | 3107-HZS-64090E |  | 3107-Z-6490 | 3107-HZS-64090E | ESD-1 зона 3107 (вращ. оборуд.) | ESD-1 for area 3107 (rotating equipment) | Button: SIS | 3000_S_SC_B03 |  |  | SIS | S | [17 empty] | REV 4 | new
2403 | TITLE-005 |  | 3107-HZS-64099 | SDO0001-01 | 3107-HZS-64099 |  | 3107-Z-6499 | 3107-HZS-64099 | ESD-1 зона 3107 (отсечные клапаны) | ESD-1 for area 3107 (shut-off valve) | Button: SIS | 3000_S_SC_B03 |  |  | SIS | S | [17 empty] | REV 4 | new
2404 | TITLE-005 |  | 3109-HZS-67001 | SDO0001-01 | 3109-HZS-67001 |  | 3109-Z-6715 | 3109-HZS-67001 | Блок. отсечных клапанов P-6701A/B/C | The on-off valve on the inlet and outlet of STY Feed pump 3109-P-6701A/B/C interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6701 | SIS | S | [17 empty] | REV 4 | new
2405 | TITLE-005 |  | 3109-HZS-67002 | SDO0001-01 | 3109-HZS-67002 |  | 3109-Z-6716 | 3109-HZS-67002 | Блок. отсечных клапанов P-6702 | The on-off valve on the inlet and outlet of EB Delivery pump 3109-P-6702 interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-6702 | SIS | S | [17 empty] | REV 4 | new
2406 | TITLE-005 |  | 3109-HZS-67004 | SDO0001-01 | 3109-HZS-67004 |  | 3109-Z-6719 | 3109-HZS-67004 | Блок. отсечных клапанов P-6704A/B | The on-off valve on the inlet and outlet of MO delivery pump 3109-P-6704A/B interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6703 | SIS | S | [17 empty] | REV 4 | new
2407 | TITLE-005 |  | 3109-HZS-67005 | SDO0001-01 | 3109-HZS-67005 |  | 3109-Z-6720 | 3109-HZS-67005 | Блок. отсечных клапанов P-6705A/B | The on-off valve on the inlet and outlet of CM delivery pump 3109-P-6705A/B interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6704 | SIS | S | [17 empty] | REV 4 | new
2408 | TITLE-005 |  | 3109-HZS-67006 | SDO0001-01 | 3109-HZS-67006 |  | 3109-Z-6721 | 3109-HZS-67006 | Блок. отсечных клапанов P-6706A/B | The on-off valve on the inlet and outlet of CM delivery pump 3109-P-6706A/B interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6705 | SIS | S | [17 empty] | REV 4 | new
2409 | TITLE-005 |  | 3109-HZS-67007 | SDO0001-01 | 3109-HZS-67007 |  | 3109-Z-6722 | 3109-HZS-67007 | Блок. отсечных клапанов P-6707 | The on-off valve on the inlet and outlet of Light component delivery pump 3109-P-6707 interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6706 | SIS | S | [17 empty] | REV 4 | new
2410 | TITLE-005 |  | 3109-HZS-67008 | SDO0001-01 | 3109-HZS-67008 |  | 3109-Z-6724 | 3109-HZS-67008 | Блок. отсечных клапанов P-6708 | The on-off valve on the inlet and outlet of Oligomer delivery pump 3109-P-6708 interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6707 | SIS | S | [17 empty] | REV 4 | new
2411 | TITLE-005 |  | 3109-HZS-67009 | SDO0001-01 | 3109-HZS-67009 |  | 3109-Z-6726 | 3109-HZS-67009 | Блок. отсечных клапанов P-6713A/B | The on-off valve on the inlet and outlet of Special MO delivery pump 3109-P-6713A/B interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6708 | SIS | S | [17 empty] | REV 4 | new
2412 | TITLE-005 |  | 3109-HZS-67090A | SDO0001-01 | 3109-HZS-67090A |  | 3109-Z-6790 | 3109-HZS-67090A | ESD-1 зона 3109 (вращ. оборуд.) | ESD-1 for area3109 (rotating equipment) | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6701 | SIS | S | [17 empty] | REV 4 | new
2413 | TITLE-005 |  | 3109-HZS-67090E | SDO0001-01 | 3109-HZS-67090E |  | 3109-Z-6790 | 3109-HZS-67090E | ESD-1 зона 3109 (вращ. оборуд.) | ESD-1 for area 3109 (rotating equipment) | Button: SIS | 3000_S_SC_B03 |  |  | SIS | S | [17 empty] | REV 4 | new
2414 | TITLE-005 |  | 3109-HZS-67091 | SDO0001-01 | 3109-HZS-67091 |  | 3109-Z-6791 | 3109-HZS-67091 | ESD-1 зона 3109 (отсечные клапаны) | ESD-1 for area 3109 (shut-off valve) | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-6701 | SIS | S | [17 empty] | REV 4 | new
2415 | TITLE-005 |  | 3104-HZS-72001A | SDO0001-01 | 3104-HZS-72001A |  | 3104-Z-7201 | 3104-HZS-72001A | Блок. останова подогревателя сырья E-7201 | Feedstock Preheater 3104-E-7201 interlock shutdown | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7201 | SIS | S | [17 empty] | REV 4 | new
2416 | TITLE-005 |  | 3104-HZS-72002 | SDO0001-01 | 3104-HZS-72002 |  | 3104-Z-7202 | 3104-HZS-72002 | Блок. останова R-7201 при Т HH1 | The First Pre-Polymerizer 3104-R-7201 interlocks and stops due to HH1 temperature | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7202 | SIS | S | [17 empty] | REV 4 | new
2417 | TITLE-005 |  | 3104-HZS-72003 | SDO0001-01 | 3104-HZS-72003 |  | 3104-Z-7203 | 3104-HZS-72003 | Блок. останова R-7201 при Т HH2 | The First Pre-Polymerizer 3104-R-7201 interlocks and stops when the temperature HH2 | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7202 | SIS | S | [17 empty] | REV 4 | new
2418 | TITLE-005 |  | 3104-HZS-72024 | SDO0001-01 | 3104-HZS-72024 |  | 3104-Z-7203 | 3104-HZS-72024 | Блок. останова R-7201 при Т HH2 | The First Pre-Polymerizer 3104-R-7201 interlocks and stops when the temperature HH2 | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2419 | TITLE-005 |  | 3104-HZS-72004 | SDO0001-01 | 3104-HZS-72004 |  | 3104-Z-7204 | 3104-HZS-72004 | Блок. останова R-7201 при Р HH | The First Pre-Polymerizer 3104-R-7201 pressure HH interlock stop | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7202 | SIS | S | [17 empty] | REV 4 | new
2420 | TITLE-005 |  | 3104-HZS-72005A | SDO0001-01 | 3104-HZS-72005A |  | 3104-Z-7205 | 3104-HZS-72005A | Блок. останова P-7201A | The First Pre-Polymerizer Melt Pump 3104-P-7201A interlocks and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7203 | SIS | S | [17 empty] | REV 4 | new
2421 | TITLE-005 |  | 3104-HZS-72006A | SDO0001-01 | 3104-HZS-72006A |  | 3104-Z-7206 | 3104-HZS-72006A | Блок. останова P-7201B | The First Pre-Polymerizer Melt Pump 3104-P-7201B interlocks and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7203 | SIS | S | [17 empty] | REV 4 | new
2422 | TITLE-005 |  | 3104-HZS-72007 | SDO0001-01 | 3104-HZS-72007 |  | 3104-Z-7207 | 3104-HZS-72007 | Блок. останова R-7202 при Т HH1 | The Second Pre-Polymerizer 3104-R-7202 interlocks and stops due to HH1 temperature | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7204 | SIS | S | [17 empty] | REV 4 | new
2423 | TITLE-005 |  | 3104-HZS-72010 | SDO0001-01 | 3104-HZS-72010 |  | 3104-Z-7208 | 3104-HZS-72010 | Блок. останова R-7202 при Т HH2 | The Second Pre-Polymerizer 3104-R-7202 interlocks and stops when the temperature is HH2 | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7204 | SIS | S | [17 empty] | REV 4 | new
2424 | TITLE-005 |  | 3104-HZS-72025 | SDO0001-01 | 3104-HZS-72025 |  | 3104-Z-7208 | 3104-HZS-72025 | Блок. останова R-7202 при Т HH2 | The Second Pre-Polymerizer 3104-R-7202 interlocks and stops when the temperature is HH2 | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2425 | TITLE-005 |  | 3104-HZS-72009 | SDO0001-01 | 3104-HZS-72009 |  | 3104-Z-7209 | 3104-HZS-72009 | Блок. останова R-7202 при Р HH | The Second Pre-Polymerizer 3104-R-7202 has HH pressure interlocking and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7204 | SIS | S | [17 empty] | REV 4 | new
2426 | TITLE-005 |  | 3104-HZS-72010A | SDO0001-01 | 3104-HZS-72010A |  | 3104-Z-7210 | 3104-HZS-72010A | Блок. останова P-7203A | The Second Pre-Polymerizer Melt Pump 3104-P-7203A interlocks and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7205 | SIS | S | [17 empty] | REV 4 | new
2427 | TITLE-005 |  | 3104-HZS-72011A | SDO0001-01 | 3104-HZS-72011A |  | 3104-Z-7211 | 3104-HZS-72011A | Блок. останова P-7203B | The Second Pre-Polymerizer Melt Pump 3104-P-7203B interlocks and stops | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7205 | SIS | S | [17 empty] | REV 4 | new
2428 | TITLE-005 |  | 3104-HZS-72012A | SDO0001-01 | 3104-HZS-72012A |  | 3104-Z-7212 | 3104-HZS-72012A | Блок. останова P-7205A/B | The First Polymerizer Melt Pump 3104-P-7205A/B interlocking stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7206 | SIS | S | [17 empty] | REV 4 | new
2429 | TITLE-005 |  | 3104-HZS-72013A | SDO0001-01 | 3104-HZS-72013A |  | 3104-Z-7213 | 3104-HZS-72013A | Блок. останова P-7205B | The First Polymerizer Melt Pump 3104-P-7205B interlocks and stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7206 | SIS | S | [17 empty] | REV 4 | new
2430 | TITLE-005 |  | 3104-HZS-72014A | SDO0001-01 | 3104-HZS-72014A |  | 3104-Z-7214 | 3104-HZS-72014A | Блок. останова P-7206A | The Second Polymerizer Melt Pump 3104-P-7206A interlocks and stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7207 | SIS | S | [17 empty] | REV 4 | new
2431 | TITLE-005 |  | 3104-HZS-72015A | SDO0001-01 | 3104-HZS-72015A |  | 3104-Z-7215 | 3104-HZS-72015A | Блок. останова P-7206B | The Second Polymerizer Melt Pump 3104-P-7206B interlocks and stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7207 | SIS | S | [17 empty] | REV 4 | new
2432 | TITLE-005 |  | 3104-HZS-72016A | SDO0001-01 | 3104-HZS-72016A |  | 3104-Z-7216 | 3104-HZS-72016A | Блок. останова P-7207A | The Third Polymerizer Melt Pump 3104-P-7207A interlocking stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7208 | SIS | S | [17 empty] | REV 4 | new
2433 | TITLE-005 |  | 3104-HZS-72017A | SDO0001-01 | 3104-HZS-72017A |  | 3104-Z-7217 | 3104-HZS-72017A | Блок. останова P-7207B | The Third Polymerizer Melt Pump 3104-P-7207B interlocks and stops | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7208 | SIS | S | [17 empty] | REV 4 | new
2434 | TITLE-005 |  | 3105-HZS-72018A | SDO0001-01 | 3105-HZS-72018A |  | 3105-Z-7218 | 3105-HZS-72018A | Блок. останова P-7208A | Main devolatilizer melt pump 3105-P-7208A interlocking shutdown | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7209 | SIS | S | [17 empty] | REV 4 | new
2435 | TITLE-005 |  | 3105-HZS-72019A | SDO0001-01 | 3105-HZS-72019A |  | 3105-Z-7219 | 3105-HZS-72019A | Блок. останова P-7208B | Main devolatilizer melt pump 3105-P-7208B interlocking shutdown | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7209 | SIS | S | [17 empty] | REV 4 | new
2436 | TITLE-005 |  | 3105-HZS-72020A | SDO0001-01 | 3105-HZS-72020A |  | 3105-Z-7220 | 3105-HZS-72020A | Блок. останова P-7209A | Final devolatilizer melt pump 3105-P-7209A interlocking shutdown | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7210 | SIS | S | [17 empty] | REV 4 | new
2437 | TITLE-005 |  | 3105-HZS-72021A | SDO0001-01 | 3105-HZS-72021A |  | 3105-Z-7221 | 3105-HZS-72021A | Блок. останова P-7209B | Final devolatilizer melt pump 3105-P-7209B interlocking shutdown | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7210 | SIS | S | [17 empty] | REV 4 | new
2438 | TITLE-005 |  | 3104-HZS-72102 | SDO0001-01 | 3104-HZS-72102 |  | 3104-Z-7247 | 3104-HZS-72102 | Блок. отсечных клапанов P-7202A/B | The on-off valve on the inlet and outlet of First Pre-Polymerizer Reflux Pump 3104-P-7202A/B interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7202 | SIS | S | [17 empty] | REV 4 | new
2439 | TITLE-005 |  | 3104-HZS-72104 | SDO0001-01 | 3104-HZS-72104 |  | 3104-Z-7248 | 3104-HZS-72104 | Блок. отсечных клапанов P-7204A/B | The on-off valve on the inlet and outlet of Second Pre-Polymerizer Reflux Pump 3104-P-7204A/B | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7204 | SIS | S | [17 empty] | REV 4 | new
2440 | TITLE-005 |  | 3105-HZS-72110 | SDO0001-01 | 3105-HZS-72110 |  | 3105-Z-7240 | 3105-HZS-72110 | Блок. отсечных клапанов P-7210AB | The on-off valve on the inlet and outlet of Final Devolatilizer Condensate Pump 3105-P-7210AB interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7211 | SIS | S | [17 empty] | REV 4 | new
2441 | TITLE-005 |  | 3105-HZS-72011 | SDO0001-01 | 3105-HZS-72011 |  | 3105-Z-7241 | 3105-HZS-72011 | Блок. отсечных клапанов P-7211AB | The on-off valve on the inlet and outlet of Purification Column Kettle Pump 3105-P-7211AB interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7212 | SIS | S | [17 empty] | REV 4 | new
2442 | TITLE-005 |  | 3105-HZS-72012 | SDO0001-01 | 3105-HZS-72012 |  | 3105-Z-7242 | 3105-HZS-72012 | Блок. отсечных клапанов P-7212AB | The on-off valve on the inlet and outlet of Purification Column Reflux Pump 3105-P-7212AB interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7213 | SIS | S | [17 empty] | REV 4 | new
2443 | TITLE-005 |  | 3105-HZS-72022 | SDO0001-01 | 3105-HZS-72022 |  | 3105-Z-7243 | 3105-HZS-72022 | Блок. отсечных клапанов P-7218AB | The on-off valve on the inlet and outlet of Devolatilization Vacuum Sealing Liquid Pump 3105-P-7218AB interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7215 | SIS | S | [17 empty] | REV 4 | new
2444 | TITLE-005 |  | 3105-HZS-72023 | SDO0001-01 | 3105-HZS-72023 |  | 3105-Z-7244 | 3105-HZS-72023 | Блок. отсечных клапанов P-7219AB | The on-off valve on the inlet and outlet of Pre-Polymerizer Vacuum Sealing Liquid Pump 3105-P-7219AB interlocking | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7215 | SIS | S | [17 empty] | REV 4 | new
2445 | TITLE-005 |  | 3105-HZS-72016 | SDO0001-01 | 3105-HZS-72016 |  | 3105-Z-7245 | 3105-HZS-72016 | Блок. отсечных клапанов P-7216AB | The on-off valve on the inlet and outlet of Oily Water Extraction Pump 3105-P-7216AB interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7216 | SIS | S | [17 empty] | REV 4 | new
2446 | TITLE-005 |  | 3105-HZS-72017 | SDO0001-01 | 3105-HZS-72017 |  | 3105-Z-7246 | 3105-HZS-72017 | Блок. отсечных клапанов P-7217 | The on-off valve on the inlet and outlet of Separator Oil Pump 3105-P-7217 interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7216 | SIS | S | [17 empty] | REV 4 | new
2447 | TITLE-005 |  | 3104-HZS-72090A | SDO0001-01 | 3104-HZS-72090A |  | 3104-Z-7290 | 3104-HZS-72090A | ESD-1 зона 3104 (вращ. оборуд.) | ESD-1 for area 3104 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7201 | SIS | S | [17 empty] | REV 4 | new
2448 | TITLE-005 |  | 3104-HZS-72090C | SDO0001-01 | 3104-HZS-72090C |  | 3104-Z-7290 | 3104-HZS-72090C | ESD-1 зона 3104 (вращ. оборуд.) | ESD-1 for area 3104 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2449 | TITLE-005 |  | 3104-HZS-72090E | SDO0001-01 | 3104-HZS-72090E |  | 3104-Z-7290 | 3104-HZS-72090E | ESD-1 зона 3104 (вращ. оборуд.) | ESD-1 for area 3104 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2450 | TITLE-005 |  | 3104-HZS-72091 | SDO0001-01 | 3104-HZS-72091 |  | 3104-Z-7291 | 3104-HZS-72091 | ESD-1 зона 3104 (отсечные клапаны) | ESD-1 for area 3104 (shut-off valve) | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7201 | SIS | S | [17 empty] | REV 4 | new
2451 | TITLE-005 |  | 3105-HZS-72092A | SDO0001-01 | 3105-HZS-72092A |  | 3105-Z-7292 | 3105-HZS-72092A | ESD-1 зона 3105 (вращ. оборуд.) | ESD-1 for area 3105 (rotating equipment) | Button: SIS | 3000_S_SC_B01 |  | 2490157-3000-PR007-7201 | SIS | S | [17 empty] | REV 4 | new
2452 | TITLE-005 |  | 3105-HZS-72093 | SDO0001-01 | 3105-HZS-72093 |  | 3105-Z-7293 | 3105-HZS-72093 | ESD-1 зона 3105 (отсечные клапаны) | ESD-1 for area 3105 (shut-off valve) | Button: SIS | 3000_S_SC_B01 |  |  | SIS | S | [17 empty] | REV 4 | new
2453 | TITLE-005 |  | 3107-HZS-74004 | SDO0001-01 | 3107-HZS-74004 |  | 3107-Z-7454 | 3107-HZS-74004 | Блок. отсечных клапанов HOP-7404AB | The on-off valve on the inlet and outlet of Feedstock Preheater HTF Pump 3107-HOP-7404AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7402 | SIS | S | [17 empty] | REV 4 | new
2454 | TITLE-005 |  | 3107-HZS-74005 | SDO0001-01 | 3107-HZS-74005 |  | 3107-Z-7455 | 3107-HZS-74005 | Блок. отсечных клапанов HOP-7405AB | The on-off valve on the inlet and outlet of First Pre-Polymerizer HTF Pump 3107-HOP-7405AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7403 | SIS | S | [17 empty] | REV 4 | new
2455 | TITLE-005 |  | 3107-HZS-74006 | SDO0001-01 | 3107-HZS-74006 |  | 3107-Z-7456 | 3107-HZS-74006 | Блок. отсечных клапанов HOP-7406AB | The on-off valve on the inlet and outlet ofSecond Pre-Polymerizer HTF Pump 3107-HOP-7406AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7403 | SIS | S | [17 empty] | REV 4 | new
2456 | TITLE-005 |  | 3107-HZS-74007 | SDO0001-01 | 3107-HZS-74007 |  | 3107-Z-7457 | 3107-HZS-74007 | Блок. отсечных клапанов HOP-7407AB | The on-off valve on the inlet and outlet of First Polymerizer HTF Pump AB 3107-HOP-7407AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7404 | SIS | S | [17 empty] | REV 4 | new
2457 | TITLE-005 |  | 3107-HZS-74017 | SDO0001-01 | 3107-HZS-74017 |  | 3107-Z-7467 | 3107-HZS-74017 | Блок. отсечных клапанов HOP-7407BC | The on-off valve on the inlet and outlet of First Polymerizer HTF Pump BC 3107-HOP-7407BC interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7404 | SIS | S | [17 empty] | REV 4 | new
2458 | TITLE-005 |  | 3107-HZS-74008 | SDO0001-01 | 3107-HZS-74008 |  | 3107-Z-7458 | 3107-HZS-74008 | Блок. отсечных клапанов HOP-7408AB | The on-off valve on the inlet and outlet of Second Polymerizer HTF Pump 3107-HOP-7408AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7405 | SIS | S | [17 empty] | REV 4 | new
2459 | TITLE-005 |  | 3107-HZS-74009 | SDO0001-01 | 3107-HZS-74009 |  | 3107-Z-7459 | 3107-HZS-74009 | Блок. отсечных клапанов HOP-7409 | The on-off valve on the inlet and outlet of Third Polymerizer Upper HTF Pump 3107-HOP-7409 interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7406 | SIS | S | [17 empty] | REV 4 | new
2460 | TITLE-005 |  | 3107-HZS-74010 | SDO0001-01 | 3107-HZS-74010 |  | 3107-Z-7460 | 3107-HZS-74010 | Блок. отсечных клапанов HOP-7410AB | The on-off valve on the inlet and outlet of Third Polymerizer Lower HTF Pump 3107-HOP-7410AB interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7406 | SIS | S | [17 empty] | REV 4 | new
2461 | TITLE-005 |  | 3107-HZS-74011 | SDO0001-01 | 3107-HZS-74011 |  | 3107-Z-7461 | 3107-HZS-74011 | Блок. отсечных клапанов HOP-7411AB | The on-off valve on the inlet and outlet of Devolatilization Heater HTF Pump 3107-HOP-7411AB interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7407 | SIS | S | [17 empty] | REV 4 | new
2462 | TITLE-005 |  | 3107-HZS-74012 | SDO0001-01 | 3107-HZS-74012 |  | 3107-Z-7462 | 3107-HZS-74012 | Блок. отсечных клапанов HOP-7412AB | The on-off valve on the inlet and outlet of Main Devolatilization Sytem HTF Pump 3107-HOP-7412AB interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7408 | SIS | S | [17 empty] | REV 4 | new
2463 | TITLE-005 |  | 3107-HZS-74013 | SDO0001-01 | 3107-HZS-74013 |  | 3107-Z-7463 | 3107-HZS-74013 | Блок. отсечных клапанов HOP-7413AB | The on-off valve on the inlet and outlet of Final Devolatilization System HTF PUMP 3107-HOP-7413AB interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7408 | SIS | S | [17 empty] | REV 4 | new
2464 | TITLE-005 |  | 3107-HZS-74014 | SDO0001-01 | 3107-HZS-74014 |  | 3107-Z-7464 | 3107-HZS-74014 | Блок. отсечных клапанов HOP-7414A | The on-off valve on the inlet and outlet of Melt Heat Exchanger HTF Pump A 3107-HOP-7414A interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7409 | SIS | S | [17 empty] | REV 4 | new
2465 | TITLE-005 |  | 3107-HZS-74114 | SDO0001-01 | 3107-HZS-74114 |  | 3107-Z-7465 | 3107-HZS-74114 | Блок. отсечных клапанов HOP-7414B | The on-off valve on the inlet and outlet of Melt Heat Exchanger HTF Pump B 3107-HOP-7414B interlocking | Button: SIS | 3000_S_SC_B03 |  | 2490157-3000-PR007-7409 | SIS | S | [17 empty] | REV 4 | new
2466 | TITLE-005 |  | 3107-HZS-74018 | SDO0001-01 | 3107-HZS-74018 |  | 3107-Z-7468 | 3107-HZS-74018 | Блок. отсечных клапанов HOP-7408BC | The on-off valve on the inlet and outlet of Second Polymerizer HTF Pump 3107-HOP-7408BC interlocking | Button: SIS | 3000_S_SC_B02 |  | 2490157-3000-PR007-7405 | SIS | S | [17 empty] | REV 4 | new
2500 | 3109 | 3109 | 3109-ZY-06791_2 | SDI0010-01R | 3109-ZY-06791-2 |  | SCS3->SCS1 3109-Z-6791 (3109-XZY-67205) | 3109-ZY-06791-2 |  |  |  | 3000_S_SC_B01 | SCS1 (NEW) |  |  | DIR (SCS1) |  | SIS | [16 empty] | Reshetov add | [14 empty] | 3000-S-SC-B01 | 3000-S-MC-B10 |  | A11 | A12 | 13 | - | A11-13 | - | A12-13 | - | 21 | [12 empty] | Запись в БД произведена
2501 | 3109 | 3109 | 3109-ZY-06791_1 | SDO0001-01 | 3109-ZY-06791-1 |  | SCS3->SCS1 3109-Z-6791 (3109-XZY-67205) | 3109-ZY-06791-1 |  |  |  | 3000_S_SC_B03 | SCS3 (NEW) |  |  | DOR (SCS3) |  | SIS | [16 empty] | Reshetov add | [14 empty] | 3000-S-SC-B03 | 3000-S-MC-B14 |  | A33 | A34 | 00 | 01 | A33-00 | A33-01 | A34-00 | A34-01 | 22 | [12 empty] | Запись в БД произведена